MINH HÙNG PLASTIC

SCH80 PVC & CPVC Piping Systems Specifications & Engineering Manual

MATERIAL CPVC COMPOUD

Best Quality from Sekisui to the World

Sekisui Chemical is the unique company in the various fields, who has the techniques of materials such as PVC polymerization, formulation, and CPVC denaturation of PVC resin, and the techniques of production, special long term evaluation, piping design and installation. Senkisui provide cpvc material for MinhHung Plastic

.

## TABLE OF CONTENTS

  - Advatages of MINH HÙNG  Sch80 PVC and CPVC Pipe	4

  - MINH HÙNG  Sch80 PVC and CPVC Pipe and Fittings	8

    - Physical Properties of PVC and CPVC Material	9

    - Schedule80 Pipe	13

    - Schedule80 Fittings	15

    - True Union	32

    - Flange	33

    - Gasket	39

  - Engineering Data	42

- Pressure Design	43

- Hydraulic Design	51

- Water Hammer	59

- Thermal Linear Expansion and Contraction	61

- Support Spacing	67

  - Installation	70

- Storage and Handling	71

- General Recommendations	73

- Rules and Guidelines	74

  - Chemical Resistance	82

  - Safety Precautions	108

Understanding Safety Alert Messages

There are several types of safety-alert messages which appear throughout this Technical Manual. Famil- iarize yourself with these types of messages and the importance of the various signal words, as explained below.

This safety alert symbol indicates important safety messages in this manual.

When you see this symbol be alert to the possibility of personal injury and carefully read and fully un- derstand the message that follows.

DANGER: Indicates an imminently hazardous situation which, if not avoided, will result in death or serious injury. Safety Signs identified by the signal word DANGER should be used sparingly and only for those situations presenting the most serious hazards.

WARNING: Indicates a potentially hazardous situation which, if not avoided, will result in death or serious injury. Hazards identified by the signal word WARNING present a lesser degree of risk of injury or death than those identified by the signal word DANGER.

CAUTION: Indicates a potentially hazardous situation which, if not avoided, may result in minor or moder- ate injury.

# Advatages of MinhHung Sch80 PVC

and CPVC Pipe

## Advatages of MINH HÙNG  Sch80 PVC and CPVC Pipe

MinhHung  PVC and CPVC pipe have a num- ber of outstanding features, such as high chemi- cal resistance, easy installation, and reasonable price, which can lead to the reduction of total construction cost. MINH HÙNG  PVC and CPVC can or should replace other materials of construction in size ranges available for all sorts of piping sys-

5	tems.

CPVC (Chlorinated Polyvinyl Chloride) is another rigid pipe which has three highly-desirable char- acteristics, good mechanical strength at high temperatures and higher chemical resistance and relatively compared to metal. CPVC polymer is more chlorinated into PVC polymer. This extra chlorine is responsible for the material’s high-tem- perature strength and other properties which are valuable for industrial piping. For pressure piping

applications, it is recommended for temperatures as high as 200°F compared with 140°F of PVC.

MINH HÙNG  Sch80 PVC & CPVC Pipe ranging in sizes from 1/2” through 24”, and PVC fittings and PVC valves are available for light, medium, and heavy duty use.

PVC and CPVC are environmentally friendly poly- mer in terms of low carbonic acid gas emission in manufacturing process

Advantages

Chemical Resistance

PVC and CPVC pipe are inert to attack by strong acids, alkalis, salt solutions, alcohols, and many other chemicals. They are dependable on corro- sive applications and impart no tastes or

odors to materials carried in them. They do not react with materials carried, nor act as a catalyst. All possibility of contamination, or chemical pro- cess changes, and all danger of clouding, slug- ging, or discoloration are eliminated.

Strength

PVC and CPVC pipe are highly resilient, tough and durable products that have high tensile and high impact strength. They will withstand surpris-

ingly high pressure for long periods.

Fire Resistance PVC and CPVC pipe products are self extinguishing and will not support com- bustion. They have an ASTM E-84 flame spread rate of 25 or less.

Internal Corrosion Resistance

PVC and CPVC pipe resist chemical attack by most acids, alkalis, salts, and organic media such as alcohols and aliphatic hydrocarbons, within certain limits of temperature and pressure. They provide the needed chemical resistance, while eliminating the disadvantages of special metals, lined piping, glass, wood, ceramics, or other spe- cial corrosion-resisting materials, which formerly had to be used.

External Corrosion Resistance

Industrial fumes, humidity, saltwater, weather, at- mospheric, or underground conditions, regard- less of type of soil or moisture encountered, can- not harm rigid PVC and CPVC plastic pipe.

Scratches or surface abrasions do not provide points which corrosive elements can attack.

Immunity to Galvanic or Electrolytic Attack PVC and CPVC pipe are inherently immune to galvanic or electrolytic action. They can be used under- ground, underwater, in the presence of metals, and can also be connected to metals.

Freedom from Toxicity, Odors, Tastes

PVC and CPVC piping are non-toxic, odorless, and tasteless. They have been listed by the Na- tional Sanitation Foundation for use with potable water.

Corrosion Free

With many other pipe materials, slight corrosion may occur. The corroded particles can contami- nate the piped fluid, complicating further process- ing, or causing bad taste, odors, or discoloration. This is particularly undesirable when the piped fluid is for domestic consumption. With PVC and CPVC, there are no corrosive by-products, there- fore, no contamination of the piped fluid.

Low Friction Loss

The smooth interior surfaces of PVC and CPVC pipe, compared to metal and other piping materi- als, assure low friction loss and high flow rates.

Additionally, since PVC and CPVC pipe

will not rust, pit, scale, or corrode, the high flow rates will be maintained for the life of the piping system.

Low Thermal Conductivity

PVC and CPVC pipe have a much lower ther- mal conductivity factor than metal pipe. There- fore, fluids being piped maintain a more constant temperature. In most cases, pipe insulation is not required.

Easy Installation and Low Installation Cost	6

PVC and CPVC pipe are lightweight, convenient to handle, relatively flexible, and easy to install. For example, it is approximately 1/5 to 1/6 for the weight of metal.

They have smooth, seamless interior walls. No special tools are required for cutting. They can be installed using solvent cementing, threading, flanging techniques.

These features lead to lower installed costs than conventional metal piping.

Maintenance Free

Once a PVC or CPVC piping system is properly selected, designed, and installed, it is virtually maintenance free. It will not rust, scale, pit, cor- rode, or promote build-up on the interior. There- fore, years of trouble-free service can be expect- ed when using MINH HÙNG  PVC and CPVC pipe.

MINHHUNG SCH80 CPVC Piping Sysyems

# MINH HÙNG  Sch80 PVC and CPVC

Pipe and Fittings

- Physical Properties of PVC and CPVC Material	9

- Schedule80 Pipe	13

- Schedule80 Fittings	15

- True Union	32

- Flange	33

- Gasket	39

## Physical Properties of

1	PVC and CPVC Material

##### Properties of PVC & CPVC PIPE

•inch-lb Unit

9

•SI Unit

10

NOTE: This data is based on information supplied by the raw material evaluation. It should be used as a general recommendation only and not as a guarantee of performance or longevity.

MINHHUNG SCH80 CPVC Piping Sysyems

## Physical Properties of

- PVC and CPVC Material

##### Properties of PVC & CPVC Fitting

•inch-lb Unit

11

•SI Unit

12

NOTE: This data is based on information supplied by the raw material evaluation. It should be used as a general recommendation only and not as a guarantee of performance or longevity.

MINHHUNG SCH80 CPVC Piping Sysyems

## Schedule80 Pipe

##### MINH HÙNG pipe is Manufactured to The Following Standard Specifications

13	*ASTM F480 Well Casing

Schedule 80 PVC and CPVC Pipe Dimensions, Weights and Maximum Operating Pressure

•inch-lb Unit

| Nominal Pipe Size | Outside Diameter | Wall Thickness | Approx. Inside Diameter | Nominal Weight | Max. operating Pressure |
| --- | --- | --- | --- | --- | --- |
|  |  |  |  | PVC | CPVC |  |
|  | inch | inch | inch | lb/ft | lb/ft | psi |
| 1/2” | 0.840 | ±0.004 | 0.147 | +0.020 | 0.53 | 0.21 | 0.23 | 850 |
| 3/4” | 1.050 | ±0.004 | 0.154 | +0.020 | 0.72 | 0.28 | 0.31 | 690 |
| 1” | 1.315 | ±0.005 | 0.179 | +0.021 | 0.94 | 0.41 | 0.45 | 630 |
| 1-1/4” | 1.660 | ±0.005 | 0.191 | +0.023 | 1.26 | 0.57 | 0.62 | 520 |
| 1-1/2” | 1.900 | ±0.006 | 0.200 | +0.024 | 1.48 | 0.69 | 0.76 | 470 |
| 2” | 2.375 | ±0.006 | 0.218 | +0.026 | 1.91 | 0.96 | 1.05 | 400 |
| 2-1/2” | 2.875 | ±0.007 | 0.276 | +0.033 | 2.29 | 1.46 | 1.60 | 420 |
| 3” | 3.500 | ±0.008 | 0.300 | +0.036 | 2.86 | 1.96 | 2.14 | 370 |
| 4” | 4.500 | ±0.009 | 0.337 | +0.040 | 3.79 | 2.86 | 3.12 | 320 |
| 5” | 5.563 | ±0.010 | 0.375 | +0.045 | 4.77 | 3.97 | 4.34 | 290 |
| 6” | 6.625 | ±0.011 | 0.432 | +0.052 | 5.71 | 5.46 | 5.96 | 280 |
| 8” | 8.625 | ±0.015 | 0.500 | +0.060 | 7.57 | 8.30 | 9.06 | 250 |
| 10” | 10.750 | ±0.015 | 0.593 | +0.071 | 9.49 | 12.30 | 13.43 | 230 |
| 12” | 12.750 | ±0.015 | 0.687 | +0.082 | 11.29 | 16.93 | 18.48 | 230 |
| 14” | 14.000 | ±0.015 | 0.750 | +0.090 | 12.41 | 20.30 | 22.16 | 220 |
| 16” | 16.000 | ±0.019 | 0.843 | +0.101 | 14.21 | 26.10 | 28.49 | 220 |
| 18” | 18.000 | ±0.019 | 0.937 | +0.112 | 16.01 | 32.66 | 35.65 | 220 |
| 20” | 20.000 | ±0.023 | 1.031 | +0.124 | 17.81 | 39.97 | 43.63 | 220 |
| 24” | 24.000 | ±0.031 | 1.218 | +0.146 | 21.42 | 56.70 | 61.89 | 210 |

NOTE: Maximum Operating Pressure is applied to 73°F

14

•SI Unit

| Nominal Pipe Size | Outside Diameter | Wall Thickness | Approx. Inside Diameter | Nominal Weight | Max. operating Pressure |
| --- | --- | --- | --- | --- | --- |
|  |  |  |  | PVC | CPVC |  |
| inch | mm | mm | mm | mm | kg/m | kg/m | MPa |
| 1/2” | 15 | 21.34 | ±0.10 | 3.73 | +0.51 | 13.4 | 0.31 | 0.34 | 5.86 |
| 3/4” | 20 | 26.67 | ±0.10 | 3.91 | +0.51 | 18.3 | 0.42 | 0.46 | 4.76 |
| 1” | 25 | 33.40 | ±0.13 | 4.55 | +0.53 | 23.8 | 0.61 | 0.67 | 4.34 |
| 1-1/4” | 32 | 42.16 | ±0.13 | 4.85 | +0.58 | 31.9 | 0.85 | 0.93 | 3.59 |
| 1-1/2” | 40 | 48.26 | ±0.15 | 5.08 | +0.61 | 37.5 | 1.03 | 1.12 | 3.24 |
| 2” | 50 | 60.33 | ±0.15 | 5.54 | +0.66 | 48.6 | 1.43 | 1.56 | 2.76 |
| 2-1/2” | 65 | 73.03 | ±0.18 | 7.01 | +0.84 | 58.2 | 2.17 | 2.37 | 2.90 |
| 3” | 80 | 88.90 | ±0.20 | 7.62 | +0.91 | 72.8 | 2.91 | 3.18 | 2.55 |
| 4” | 100 | 114.30 | ±0.23 | 8.56 | +1.02 | 96.2 | 4.26 | 4.65 | 2.21 |
| 5” | 125 | 141.30 | ±0.25 | 9.53 | +1.14 | 121.1 | 5.91 | 6.45 | 2.00 |
| 6” | 150 | 168.28 | ±0.28 | 10.97 | +1.32 | 145.0 | 8.13 | 8.87 | 1.93 |
| 8” | 200 | 219.08 | ±0.38 | 12.70 | +1.52 | 192.2 | 12.35 | 13.48 | 1.72 |
| 10” | 250 | 273.05 | ±0.38 | 15.06 | +1.80 | 241.1 | 18.31 | 19.98 | 1.59 |
| 12” | 300 | 323.85 | ±0.38 | 17.45 | +2.08 | 286.9 | 25.19 | 27.49 | 1.59 |
| 14” | 350 | 355.60 | ±0.38 | 19.05 | +2.29 | 315.2 | 30.22 | 32.98 | 1.52 |
| 16” | 400 | 406.40 | ±0.48 | 21.41 | +2.57 | 361.0 | 38.85 | 42.41 | 1.52 |
| 18” | 450 | 457.20 | ±0.48 | 23.80 | +2.84 | 406.8 | 48.60 | 53.05 | 1.52 |
| 20” | 500 | 508.00 | ±0.58 | 26.19 | +3.15 | 452.5 | 59.48 | 64.92 | 1.52 |
| 24” | 600 | 609.60 | ±0.79 | 30.94 | +3.71 | 544.0 | 84.38 | 92.11 | 1.45 |

NOTE: Maximum Operating Pressure is applied to 23°C

MINHHUNG SCH80 CPVC Piping Sysyems

## 3	Schedule80 Fittings

##### MINH HÙNG  Thermoplastic Fittings are manufactured to The Following Standard Specifications

15

Socket Dimensions

l	l

PVC AND CPVC SCHEDULE 80 TAPER SOCKET DIMENSIONS (SOLVENT CEMENT STYLE)

ASTM D-2467 (PVC) F-439 (CPVC)

•inch-lb Unit	•SI Unit

Thread Dimensions

S

T	L

P

D

90°

16

FEMALE TAPER THREADS ASTM D-2464 (PVC) F-437 (CPVC) ASTM F-1496

•inch-lb Unit

•SI Unit

MALE TAPER THREADS

ASTM D-2464 (PVC) F-437 (CPVC) ASTM F-1496

AMERICAN NATIONAL STANDARD TAPER PIPE THREADS (NPT) ASME (ANSI) B1.20.1

ASTM F-1498

| Nominal Pipe Size | inch Pipe O.D. (D) | Female Thread Min. Length (T) | Male Thread Min. Length (S) | Overall Pipe Thread Length (L) | Pitch of Thread (P) | Threads Per In. | Height of Thread |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1/2” | 21.34 | 23 | 18.5 | 19.8501 | 1.8143 | 14.0 | 1.4514 |
| 3/4” | 26.67 | 26 | 18.5 | 20.1549 | 1.8143 | 14.0 | 1.4514 |
| 1” | 33.40 | 29 | 21.0 | 25.0063 | 2.2088 | 11.5 | 1.7671 |
| 1-1/4” | 42.16 | 32 | 24.5 | 25.6159 | 2.2088 | 11.5 | 1.7671 |
| 1-1/2” | 48.26 | 35 | 24.5 | 26.0401 | 2.2088 | 11.5 | 1.7671 |
| 2” | 60.33 | 40 | 27.0 | 26.8783 | 2.2088 | 11.5 | 1.7671 |
| 2-1/2” | 73.03 | 45 | 40.0 | 39.9085 | 3.1750 | 8.0 | 2.5400 |
| 3” | 88.90 | 48 | 42.0 | 41.4960 | 3.1750 | 8.0 | 2.5400 |
| 4” | 114.30 | 58 | 44.5 | 44.0360 | 3.1750 | 8.0 | 2.5400 |

MINHHUNG SCH80 CPVC Piping Sysyems

## 3	Schedule80 Fittings

### Coupling

S

17	N

Coupling FT

N

•inch-lb Unit

| Size | Inch | Weight (lb/pc) |
| --- | --- | --- |
|  | L | N | PVC | CPVC |
| 1/2” | 1.969 | 0.220 | 0.05 | 0.06 |
| 3/4” | 2.205 | 0.205 | 0.07 | 0.07 |
| 1” | 2.480 | 0.230 | 0.10 | 0.11 |
| 1-1/4” | 2.717 | 0.217 | 0.18 | 0.19 |
| 1-1/2” | 2.953 | 0.202 | 0.24 | 0.26 |
| 2” | 3.346 | 0.346 | 0.35 | 0.38 |
| 2-1/2” | 3.780 | 0.280 | 0.56 | 0.61 |
| 3” | 4.016 | 0.265 | 0.85 | 0.92 |
| 4” | 4.843 | 0.343 | 1.22 | 1.33 |
| 5” | 5.669 | 0.315 | 1.89 | 2.07 |
| 6” | 6.496 | 0.354 | 3.02 | 3.30 |
| 8” | 8.504 | 0.394 | 7.30 | 7.97 |
| 10” | 11.614 | 0.591 | 14.52 | 15.85 |
| 12” | 12.992 | 0.787 | 22.00 | 24.01 |

•inch-lb Unit

•SI Unit

| Size | mm | Weight (kg/pc) |
| --- | --- | --- |
|  | L | N | PVC | CPVC |
| 1/2” | 50.0 | 5.6 | 0.024 | 0.026 |
| 3/4” | 56.0 | 5.2 | 0.031 | 0.034 |
| 1” | 63.0 | 5.8 | 0.045 | 0.049 |
| 1-1/4” | 69.0 | 5.5 | 0.080 | 0.087 |
| 1-1/2” | 75.0 | 5.1 | 0.110 | 0.120 |
| 2” | 85.0 | 8.8 | 0.160 | 0.175 |
| 2-1/2” | 96.0 | 7.1 | 0.255 | 0.278 |
| 3” | 102.0 | 6.7 | 0.384 | 0.419 |
| 4” | 123.0 | 8.7 | 0.553 | 0.604 |
| 5” | 144.0 | 8.0 | 0.860 | 0.939 |
| 6” | 165.0 | 9.0 | 1.372 | 1.498 |
| 8” | 216.0 | 10.0 | 3.320 | 3.624 |
| 10” | 295.0 | 15.0 | 6.600 | 7.204 |
| 12” | 330.0 | 20.0 | 10.000 | 10.915 |

•SI Unit

### Reducing Coupling

###### Reducing Coupling S X S

L

•inch-lb Unit	•SI Unit

18

Combination Table of Coupling

+:Coupling without Bushing +B: with one Bushing +B*2: with 2 pieces of Bushing

|  | Reducing Size |
| --- | --- |
|  | 1/2" | 3/4" | 1" | 1-1/4" | 1-1/2" | 2" | 2-1/2" | 3" | 4" | 5" | 6" | 8" | 10" | 12" |
|  | 1/2" | + |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 3/4" | + | + |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 1" | + | + | + |  |  |  |  |  |  |  |  |  |  |  |
|  | 1-1/4" | + | + | + | + |  |  |  |  |  |  |  |  |  |  |
|  | 1-1/2" | + | + | + | + | + |  |  |  |  |  |  |  |  |  |
|  | 2" | + | + | + | + | + | + |  |  |  |  |  |  |  |  |
|  | 2-1/2" | +B | +B | +B | +B | + | + | + |  |  |  |  |  |  |  |
|  | 3" | +B | +B | + | +B | + | + | + | + |  |  |  |  |  |  |
|  | 4" | +B | +B | +B | +B | +B | + | + | + | + |  |  |  |  |  |
|  | 5" |  |  | +B | +B | +B | +B | +B | +B | + | + |  |  |  |  |
|  | 6" |  |  | +B*2 | +B*2 | +B*2 | +B*2 | +B*2 | + | + | + | + |  |  |  |
|  | 8" |  |  | +B*2 | +B*2 | +B*2 | +B*2 | +B*2 | +B*2 | + | +B | + | + |  |  |
|  | 10" |  |  |  |  |  | +B*2 | +B*2 | +B*2 | +B | +B*2 | +B | + | + |  |
|  | 12" |  |  |  |  |  | +B*2 | +B*2 | +B*2 | +B | +B*2 | +B | + | + | + |

MINHHUNG SCH80 CPVC Piping Sysyems

## 3	Schedule80 Fittings

### 90°Elbow

###### 90°Elbow S X S

•inch-lb Unit

•SI Unit

19

H

G

###### 90°Elbow FT X FT

•inch-lb Unit

•SI Unit

H

G

###### 90°Elbow S X FT

H

G

•inch-lb Unit

•SI Unit

### 45°Elbow

###### 45°Elbow S X S

45°Elbow FT X FT

•inch-lb Unit

| Size | Inch | Weight (lb/pc) |
| --- | --- | --- |
|  | J | H | PVC | CPVC |
| 1/2” | 0.267 | 1.142 | 0.07 | 0.07 |
| 3/4” | 0.339 | 1.339 | 0.09 | 0.10 |
| 1” | 0.331 | 1.457 | 0.14 | 0.15 |
| 1-1/4” | 0.443 | 1.693 | 0.22 | 0.25 |
| 1-1/2” | 0.475 | 1.850 | 0.29 | 0.31 |
| 2” | 0.665 | 2.165 | 0.42 | 0.46 |
| 2-1/2” | 0.770 | 2.520 | 0.79 | 0.86 |
| 3” | 0.959 | 2.835 | 1.28 | 1.39 |
| 4” | 1.136 | 3.386 | 2.01 | 2.20 |
| 5” | 1.496 | 4.173 | 3.51 | 3.83 |
| 6” | 1.811 | 4.882 | 5.68 | 6.20 |
| 8” | 2.165 | 6.220 | 10.84 | 11.83 |
| 10” | 2.756 | 8.268 | 16.38 | 18.30 |
| 12” | 3.346 | 9.449 | 33.73 | 36.81 |

•inch-lb Unit

| Size | Inch | Weight (lb/pc) |
| --- | --- | --- |
|  | J | H | PVC | CPVC |
| 1/2” | 0.267 | 1.142 | 0.09 | 0.10 |
| 3/4” | 0.339 | 1.339 | 0.13 | 0.14 |
| 1” | 0.331 | 1.457 | 0.21 | 0.23 |
| 1-1/4” | 0.443 | 1.693 | 0.32 | 0.35 |
| 1-1/2” | 0.475 | 1.850 | 0.44 | 0.48 |
| 2” | 0.665 | 2.165 | 0.66 | 0.72 |
| 2-1/2” | 0.770 | 2.520 | 1.18 | 1.29 |
| 3” | 0.959 | 2.835 | 2.02 | 2.21 |
| 4” | 1.136 | 3.386 | 3.31 | 3.61 |

•SI Unit

20

•SI Unit

| Size | mm | Weight (kg/pc) |
| --- | --- | --- |
|  | J | H | PVC | CPVC |
| 1/2” | 7 | 29 | 0.040 | 0.044 |
| 3/4” | 9 | 34 | 0.058 | 0.063 |
| 1” | 8 | 37 | 0.094 | 0.103 |
| 1-1/4” | 11 | 43 | 0.146 | 0.160 |
| 1-1/2” | 12 | 47 | 0.200 | 0.218 |
| 2” | 17 | 55 | 0.298 | 0.326 |
| 2-1/2” | 20 | 64 | 0.537 | 0.586 |
| 3” | 24 | 72 | 0.920 | 1.004 |
| 4” | 29 | 86 | 1.503 | 1.640 |

MINHHUNG SCH80 CPVC Piping Sysyems

## 3	Schedule80 Fittings

### Tee

Tee S X S X S

21

H

•inch-lb Unit	•SI Unit

Tee FT X FT X FT

H

•inch-lb Unit	•SI Unit

Tee S X S X FT

H

•inch-lb Unit	•SI Unit

22

MINHHUNG SCH80 CPVC Piping Sysyems

## 3	Schedule80 Fittings

### Reducing Tee

###### Reducing Tee S X S X S

23

H1

•inch-lb Unit

Combination Table of Tee

+:Tee without Bushing +B: with one Bushing +B*2: with 2 pieces of Bushing

|  | Branch Size |
| --- | --- |
|  | 1/2" | 3/4" | 1" | 1-1/4" | 1-1/2" | 2" | 2-1/2" | 3" | 4" | 5" | 6" | 8" | 10" | 12" |
|  | 1/2" | + |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 3/4" | + | + |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 1" | + | + | + |  |  |  |  |  |  |  |  |  |  |  |
|  | 1-1/4" | + | + | + | + |  |  |  |  |  |  |  |  |  |  |
|  | 1-1/2" | + | + | + | + | + |  |  |  |  |  |  |  |  |  |
|  | 2" | + | + | + | + | + | + |  |  |  |  |  |  |  |  |
|  | 2-1/2" | +B | +B | +B | +B | + | + | + |  |  |  |  |  |  |  |
|  | 3" | +B | +B | +B | +B | + | + | + | + |  |  |  |  |  |  |
|  | 4" | +B | +B | +B | +B | +B | + | + | + | + |  |  |  |  |  |
|  | 5" |  |  | +B | +B | +B | +B | +B | +B | + | + |  |  |  |  |
|  | 6" |  |  | +B | +B | +B | +B | +B | + | + | + | + |  |  |  |
|  | 8" |  |  | +B | +B | +B | +B | +B | +B | + | +B | + | + |  |  |
|  | 10" |  |  |  |  |  | +B | +B | +B | + | +B*2 | +B | + | + |  |
|  | 12" |  |  |  |  |  | +B | +B | +B | + | +B*2 | +B | + | + | + |

•SI Unit

| Size | mm | Weight (kg/pc) |
| --- | --- | --- |
|  | G1 | G2 | H1 | H2 | PVC | CPVC |
| 3/4" x 1/2" | 17.1 | 17.8 | 42.5 | 40.0 | 0.060 | 0.067 |
| 1" x 1/2" | 21.4 | 21.8 | 50.0 | 44.0 | 0.096 | 0.107 |
| 1" x 3/4" | 21.4 | 38.6 | 50.0 | 46.0 | 0.098 | 0.109 |
| 1-1/4" x 1/2" | 26.3 | 25.8 | 58.0 | 48.0 | 0.152 | 0.170 |
| 1-1/4" x 3/4" | 26.3 | 26.6 | 58.0 | 52.0 | 0.154 | 0.172 |
| 1-1/4" x 1" | 26.3 | 27.4 | 58.0 | 56.0 | 0.159 | 0.178 |
| 1-1/2" x 1/2" | 30.1 | 29.8 | 65.0 | 52.0 | 0.200 | 0.223 |
| 1-1/2" x 3/4" | 30.1 | 29.6 | 65.0 | 55.0 | 0.202 | 0.226 |
| 1-1/2" x 1" | 30.1 | 29.4 | 65.0 | 58.0 | 0.207 | 0.231 |
| 1-1/2" x 1-1/4" | 30.1 | 30.3 | 65.0 | 62.0 | 0.216 | 0.241 |
| 2" x 1/2" | 35.9 | 35.8 | 74.0 | 58.0 | 0.281 | 0.314 |
| 2" x 3/4" | 35.9 | 35.6 | 74.0 | 61.0 | 0.283 | 0.316 |
| 2" x 1" | 35.9 | 36.4 | 74.0 | 65.0 | 0.292 | 0.326 |
| 2" x 1-1/4" | 35.9 | 36.3 | 74.0 | 68.0 | 0.303 | 0.338 |
| 2" x 1-1/2" | 35.9 | 37.1 | 74.0 | 72.0 | 0.312 | 0.349 |
| 2-1/2" x 1-1/2" | 44.6 | 42.1 | 89.0 | 77.0 | 0.534 | 0.596 |
| 2-1/2" x 2" | 44.6 | 43.9 | 89.0 | 82.0 | 0.552 | 0.617 |
| 3" x 1-1/2" | 53.4 | 50.1 | 101.0 | 85.0 | 0.711 | 0.794 |
| 3" x 2" | 53.4 | 51.9 | 101.0 | 90.0 | 0.733 | 0.819 |
| 3" x 2-1/2" | 53.4 | 52.6 | 101.0 | 97.0 | 0.768 | 0.858 |
| 4" x 2" | 63.8 | 62.9 | 121.0 | 101.0 | 1.328 | 1.483 |
| 4" x 2-1/2" | 63.9 | 63.6 | 121.0 | 108.0 | 1.326 | 1.481 |
| 4" x 3" | 63.9 | 64.4 | 121.0 | 112.0 | 1.380 | 1.541 |
| 5" x 4" | 79.5 | 79.9 | 147.5 | 137.0 | 1.984 | 2.216 |
| 6" x 3" | 95.0 | 95.4 | 173.0 | 143.0 | 3.350 | 3.742 |
| 6" x 4" | 95.0 | 95.9 | 173.0 | 153.0 | 3.328 | 3.717 |
| 6" x 5" | 95.0 | 97.0 | 173.0 | 165.0 | 3.400 | 3.798 |
| 8" x 3" | 122.0 | 122.4 | 225.0 | 170.0 | 7.720 | 8.623 |
| 8" x 4" | 122.0 | 122.9 | 225.0 | 180.0 | 7.860 | 8.780 |
| 8" x 6" | 122.0 | 123.0 | 225.0 | 201.0 | 8.120 | 9.070 |
| 10" x 4" | 150.0 | 153.9 | 290.0 | 211.0 | 14.010 | 15.649 |
| 10" x 8" | 150.0 | 158.0 | 290.0 | 261.0 | 14.150 | 15.806 |
| 12" x 4" | 175.0 | 183.0 | 330.0 | 211.0 | 21.900 | 24.462 |
| 12" x 8" | 175.0 | 183.0 | 330.0 | 286.0 | 21.600 | 24.127 |
| 12" x 10" | 175.0 | 175.0 | 330.0 | 315.0 | 21.400 | 23.904 |

24

MINHHUNG SCH80 CPVC Piping Sysyems

## 3	Schedule80 Fittings

### Reducing Tee

###### Reducing Tee S X S X FT

25

H1

•inch-lb Unit

•SI Unit

| Size | mm | Weight (kg/pc) |
| --- | --- | --- |
|  | G1 | G2 | H1 | H2 | PVC | CPVC |
| 3/4" x 1/2" | 17.1 | 17.8 | 42.5 | 40.0 | 0.068 | 0.075 |
| 1" x 1/2" | 21.4 | 21.8 | 50.0 | 44.0 | 0.104 | 0.116 |
| 1" x 3/4" | 21.4 | 38.6 | 50.0 | 46.0 | 0.110 | 0.123 |
| 1-1/4" x 1/2" | 26.3 | 25.8 | 58.0 | 48.0 | 0.160 | 0.178 |
| 1-1/4" x 3/4" | 26.3 | 26.6 | 58.0 | 52.0 | 0.166 | 0.185 |
| 1-1/4" x 1" | 26.3 | 27.4 | 58.0 | 56.0 | 0.179 | 0.200 |
| 1-1/2" x 1/2" | 30.1 | 29.8 | 65.0 | 52.0 | 0.208 | 0.232 |
| 1-1/2" x 3/4" | 30.1 | 29.6 | 65.0 | 55.0 | 0.214 | 0.239 |
| 1-1/2" x 1" | 30.1 | 29.4 | 65.0 | 58.0 | 0.227 | 0.253 |
| 1-1/2" x 1-1/4" | 30.1 | 30.3 | 65.0 | 62.0 | 0.246 | 0.275 |
| 2" x 1/2" | 35.9 | 35.8 | 74.0 | 58.0 | 0.289 | 0.322 |
| 2" x 3/4" | 35.9 | 35.6 | 74.0 | 61.0 | 0.295 | 0.329 |
| 2" x 1" | 35.9 | 36.4 | 74.0 | 65.0 | 0.312 | 0.348 |
| 2" x 1-1/4" | 35.9 | 36.3 | 74.0 | 68.0 | 0.333 | 0.372 |
| 2" x 1-1/2" | 35.9 | 37.1 | 74.0 | 72.0 | 0.352 | 0.393 |
| 2-1/2" x 1-1/2" | 44.6 | 42.1 | 89.0 | 77.0 | 0.574 | 0.641 |
| 2-1/2" x 2" | 44.6 | 43.9 | 89.0 | 82.0 | 0.611 | 0.682 |
| 3" x 1-1/2" | 53.4 | 50.1 | 101.0 | 85.0 | 0.751 | 0.839 |
| 3" x 2" | 53.4 | 51.9 | 101.0 | 90.0 | 0.792 | 0.885 |
| 3" x 2-1/2" | 53.4 | 52.6 | 101.0 | 97.0 | 0.872 | 0.974 |
| 4" x 2" | 63.8 | 62.9 | 121.0 | 101.0 | 1.387 | 1.549 |
| 4" x 2-1/2" | 63.9 | 63.6 | 121.0 | 108.0 | 1.430 | 1.597 |
| 4" x 3" | 63.9 | 64.4 | 121.0 | 112.0 | 1.523 | 1.701 |
| 5" x 4" | 79.5 | 79.9 | 147.5 | 137.0 | 2.109 | 2.356 |
| 6" x 3" | 95.0 | 95.4 | 173.0 | 143.0 | 3.493 | 3.901 |
| 6" x 4" | 95.0 | 95.9 | 173.0 | 153.0 | 3.579 | 3.997 |
| 8" x 3" | 122.0 | 122.4 | 225.0 | 170.0 | 7.863 | 8.782 |
| 8" x 4" | 122.0 | 122.9 | 225.0 | 180.0 | 8.111 | 9.059 |
| 10" x 4" | 150.0 | 153.9 | 290.0 | 211.0 | 14.135 | 15.789 |
| 12" x 4" | 175.0 | 183.0 | 330.0 | 211.0 | 21.525 | 24.043 |

26

MINHHUNG SCH80 CPVC Piping Sysyems

## 3	Schedule80 Fittings

### Reducing Bushing

###### Reducing Bushing

S X S

27

L

•inch-lb Unit	•SI Unit

Combination Table for Reducing Bushing

+:Bushing without Bushing +B: with an additional Bushing +B*2: with two additional Bushing

28

###### Reducing Bushing S X FT

L

•inch-lb Unit	•SI Unit

MINHHUNG SCH80 CPVC Piping Sysyems

## 3	Schedule80 Fittings

### Male Adapter

###### Male Adapter Mpt X S

29

L

•inch-lb Unit	•SI Unit

### Female Adapter

###### Female Adapter S X FT

G

•inch-lb Unit	•SI Unit

### Cap

###### Socket Cap

L

###### Threaded Cap

•inch-lb Unit

| Size | Inch | Weight (lb/pc) |
| --- | --- | --- |
|  | L | PVC | CPVC |
| 1/2” | 1.181 | 0.04 | 0.04 |
| 3/4” | 1.339 | 0.05 | 0.06 |
| 1” | 1.496 | 0.08 | 0.09 |
| 1-1/4” | 1.654 | 0.13 | 0.14 |
| 1-1/2” | 1.811 | 0.20 | 0.22 |
| 2” | 2.047 | 0.26 | 0.29 |
| 2-1/2” | 2.362 | 0.45 | 0.49 |
| 3” | 2.579 | 0.79 | 0.87 |
| 4” | 3.134 | 1.03 | 1.12 |
| 5” | 3.504 | 1.69 | 1.84 |
| 6” | 3.969 | 2.63 | 2.87 |
| 8” | 5.197 | 5.13 | 5.73 |
| 10” | 6.614 | 10.11 | 11.29 |
| 12” | 7.323 | 15.60 | 17.42 |

•inch-lb Unit

| Size | Inch | Weight (lb/pc) |
| --- | --- | --- |
|  | L | PVC | CPVC |
| 1/2” | 1.181 | 0.04 | 0.05 |
| 3/4” | 1.339 | 0.06 | 0.07 |
| 1” | 1.496 | 0.10 | 0.11 |
| 1-1/4” | 1.654 | 0.16 | 0.18 |
| 1-1/2” | 1.811 | 0.24 | 0.26 |
| 2” | 2.047 | 0.33 | 0.36 |
| 2-1/2” | 2.362 | 0.57 | 0.62 |
| 3” | 2.579 | 0.95 | 1.04 |
| 4” | 3.134 | 1.30 | 1.42 |

•SI Unit

30

•SI Unit

| Size | mm | Weight (kg/pc) |
| --- | --- | --- |
|  | L | PVC | CPVC |
| 1/2” | 30.0 | 0.020 | 0.022 |
| 3/4” | 34.0 | 0.029 | 0.032 |
| 1” | 38.0 | 0.046 | 0.050 |
| 1-1/4” | 42.0 | 0.073 | 0.080 |
| 1-1/2” | 46.0 | 0.110 | 0.120 |
| 2” | 52.0 | 0.149 | 0.163 |
| 2-1/2” | 60.0 | 0.257 | 0.281 |
| 3” | 65.5 | 0.431 | 0.471 |
| 4” | 79.6 | 0.592 | 0.646 |

MINHHUNG SCH80 CPVC Piping Sysyems

## 3	Schedule80 Fittings

### Plug

###### Cap and Plug Mpt Plug

31

L

•inch-lb Unit	•SI Unit

### Nipple

CLOSE

L

SHORT

L

LONG

L

•inch-lb Unit	•SI Unit

## 4	True Union

### Union (O-Ring Seat)

###### Union (O-Ring Seat) S X S

•inch-lb Unit

L

O-ring: EPDM. FKM

###### Union (O-Ring Seat) FT X FT

•inch-lb Unit

G L

O-ring: EPDM. FKM

•SI Unit

32

•SI Unit

| Size | mm | Weight (kg/pc) |
| --- | --- | --- |
|  | L | G | PVC | CPVC |
| 1/2" | 52 | 8 | 0.046 | 0.050 |
| 3/4" | 59 | 9 | 0.073 | 0.080 |
| 1" | 67 | 9 | 0.130 | 0.142 |
| 1-1/4" | 76 | 12 | 0.204 | 0.223 |
| 1-1/2" | 82 | 12 | 0.269 | 0.294 |
| 2" | 92 | 16 | 0.426 | 0.465 |
| 2-1/2" | 108 | 18 | 0.656 | 0.716 |
| 3" | 120 | 24 | 1.076 | 1.175 |
| 4" | 152 | 36 | 1.862 | 2.032 |

MINHHUNG SCH80 CPVC Piping Sysyems

## 5	Flange

### One Piece Flange

###### Flange (ANSI) - Socket (ASTM)

•inch-lb Unit

33

n-φh NOTE: Flange bolt hole patterns meet ANSI B16.5, class 150

L

•SI Unit

| Size | mm | Weight (kg/pc) |
| --- | --- | --- |
|  | L | t | PCD | D | n | h | PVC | CPVC |
| 1/2" | 25.2 | 11.7 | 60.5 | 89.0 | 4 | 16 | 0.094 | 0.105 |
| 3/4" | 29.5 | 13.1 | 70.0 | 98.0 | 4 | 16 | 0.120 | 0.134 |
| 1" | 32.0 | 15.2 | 79.5 | 108.0 | 4 | 16 | 0.190 | 0.212 |
| 1-1/4" | 38.4 | 16.9 | 89.0 | 117.0 | 4 | 16 | 0.240 | 0.268 |
| 1-1/2" | 40.5 | 18.3 | 98.5 | 127.0 | 4 | 16 | 0.310 | 0.346 |
| 2" | 45.0 | 19.0 | 120.5 | 152.0 | 4 | 19 | 0.458 | 0.512 |
| 2-1/2" | 50.5 | 25.0 | 139.5 | 178.0 | 4 | 19 | 0.715 | 0.799 |
| 3" | 50.5 | 25.5 | 152.5 | 191.0 | 4 | 19 | 0.880 | 0.983 |
| 4" | 63.3 | 28.4 | 190.5 | 229.0 | 8 | 19 | 1.340 | 1.497 |
| 5" | 76.0 | 28.5 | 216.0 | 254.0 | 8 | 22 | 1.648 | 1.841 |
| 6" | 84.5 | 26.0 | 241.5 | 279.0 | 8 | 22 | 2.220 | 2.480 |
| 8" | 116.0 | 29.0 | 298.5 | 343.0 | 8 | 22 | 3.400 | 3.798 |

NOTE: Flange bolt hole patterns meet ANSI B16.5, class 150

###### Flange (JIS) - Socket (ASTM)

•inch-lb Unit

34

n-φh NOTE: Flange bolt hole patterns meet JIS B2220

L

•SI Unit

| Size | mm | Weight (kg/pc) |
| --- | --- | --- |
|  | L | t | PCD | D | n | h | PVC | CPVC |
| 1/2" | 25.2 | 14 | 70 | 95 | 4 | 15 | 0.096 | 0.107 |
| 3/4" | 29.5 | 14 | 75 | 100 | 4 | 15 | 0.123 | 0.137 |
| 1" | 32.0 | 14 | 90 | 125 | 4 | 19 | 0.195 | 0.218 |
| 1-1/4" | 38.4 | 16 | 100 | 135 | 4 | 19 | 0.247 | 0.276 |
| 1-1/2" | 40.5 | 16 | 105 | 140 | 4 | 19 | 0.320 | 0.358 |
| 2" | 45.0 | 20 | 120 | 155 | 4 | 19 | 0.473 | 0.528 |
| 2-1/2" | 50.5 | 22 | 140 | 175 | 4 | 19 | 0.741 | 0.828 |
| 3" | 50.5 | 22 | 150 | 185 | 8 | 19 | 0.916 | 1.023 |
| 4" | 63.3 | 22 | 175 | 210 | 8 | 19 | 1.403 | 1.567 |
| 5" | 76.0 | 24 | 210 | 250 | 8 | 23 | 1.730 | 1.933 |
| 6" | 84.5 | 26 | 240 | 280 | 8 | 23 | 2.331 | 2.604 |
| 8" | 116.0 | 28 | 290 | 330 | 12 | 23 | 3.570 | 3.988 |

NOTE: Flange bolt hole patterns meet JIS B2220

MINHHUNG SCH80 CPVC Piping Sysyems

## 5	Flange

### One Piece Flange

###### Flange (ANSI) -Threaded

•inch-lb Unit

35

NOTE: Flange bolt hole patterns meet ANSI B16.5, class 150

n-φh

L

•SI Unit

| Size | mm | Weight (kg/pc) |
| --- | --- | --- |
|  | L | t | PCD | D | n | h | PVC | CPVC |
| 1/2" | 25.2 | 11.7 | 60.5 | 89.0 | 4 | 16 | 0.098 | 0.109 |
| 3/4" | 29.5 | 13.1 | 70.0 | 98.0 | 4 | 16 | 0.126 | 0.141 |
| 1" | 32.0 | 15.2 | 79.5 | 108.0 | 4 | 16 | 0.200 | 0.223 |
| 1-1/4" | 38.4 | 16.9 | 89.0 | 117.0 | 4 | 16 | 0.255 | 0.285 |
| 1-1/2" | 40.5 | 18.3 | 98.5 | 127.0 | 4 | 16 | 0.330 | 0.369 |
| 2" | 45.0 | 19.0 | 120.5 | 152.0 | 4 | 19 | 0.487 | 0.544 |
| 2-1/2" | 50.5 | 25.0 | 139.5 | 178.0 | 4 | 19 | 0.767 | 0.857 |
| 3" | 50.5 | 25.5 | 152.5 | 191.0 | 4 | 19 | 0.951 | 1.063 |
| 4" | 63.3 | 28.4 | 190.5 | 229.0 | 8 | 19 | 1.465 | 1.637 |

NOTE: Flange bolt hole patterns meet ANSI B16.5, class 150

### Van Stone Flange

###### Flange (ANSI) - Socket (ASTM)

•inch-lb Unit

36

NOTE: Flange bolt hole patterns meet ANSI B16.5, class 150

n-φh

L

•SI Unit

| Size | mm | Weight (kg/pc) |
| --- | --- | --- |
|  | L | t | PCD | D | n | h | PVC | CPVC |
| 2" | 43.0 | 21.0 | 120.5 | 152.0 | 4 | 19 | 0.390 | 0.433 |
| 2-1/2" | 51.0 | 25.0 | 139.5 | 178.0 | 4 | 19 | 0.595 | 0.696 |
| 3" | 55.0 | 27.0 | 152.5 | 191.0 | 4 | 19 | 0.734 | 0.810 |
| 4" | 64.0 | 29.0 | 190.5 | 229.0 | 8 | 19 | 1.066 | 1.178 |
| 5" | 76.0 | 29.0 | 216.0 | 254.0 | 8 | 22 | 1.423 | 1.590 |
| 6" | 85.0 | 32.0 | 241.5 | 279.0 | 8 | 22 | 1.820 | 1.996 |
| 8" | 119.0 | 32.0 | 298.5 | 343.0 | 8 | 22 | 2.870 | 3.219 |
| 10" | 150.0 | 42.0 | 362.0 | 406.0 | 12 | 25 | 4.923 | 5.451 |
| 12" | 190.0 | 42.0 | 432.0 | 483.0 | 12 | 25 | 8.800 | 9.500 |

NOTE: Flange bolt hole patterns meet ANSI B16.5, class 150

MINHHUNG SCH80 CPVC Piping Sysyems

## Flange

### Van Stone Flange

###### Flange (JIS) - Socket (ASTM)

•inch-lb Unit

37

NOTE: Flange bolt hole patterns meet JIS B2220

n-φh

L

•SI Unit

| Size | mm | Weight (kg/pc) |
| --- | --- | --- |
|  | L | t | PCD | D | n | h | PVC | CPVC |
| 2" | 43.0 | 20 | 120 | 155 | 4 | 19 | 0.405 | 0.452 |
| 2-1/2" | 51.0 | 22 | 140 | 175 | 4 | 19 | 0.621 | 0.693 |
| 3" | 55.0 | 22 | 150 | 185 | 8 | 19 | 0.770 | 0.860 |
| 4" | 64.0 | 22 | 175 | 210 | 8 | 19 | 1.129 | 1.261 |
| 5" | 76.0 | 24 | 210 | 250 | 8 | 23 | 1.506 | 1.682 |
| 6" | 85.0 | 26 | 240 | 280 | 8 | 23 | 1.931 | 2.157 |
| 8" | 119.0 | 28 | 290 | 330 | 12 | 23 | 3.040 | 3.396 |
| 10" | 150.0 | 30 | 355 | 400 | 12 | 25 | 5.169 | 5.774 |
| 12" | 190.0 | 32 | 400 | 445 | 16 | 25 | 9.240 | 10.321 |

NOTE: Flange bolt hole patterns meet JIS B2220

### Blind Flange

n-φh

•inch-lb Unit

38

NOTE: Flange bolt hole patterns meet ANSI B16.5

•SI Unit

| Size | mm | Weight (kg/pc) |
| --- | --- | --- |
|  | t | PCD | D | n | h | PVC | CPVC |
| 1/2" | 14.5 | 60.5 | 89.0 | 4 | 16 | 0.108 | 0.121 |
| 3/4" | 16.0 | 70.0 | 98.0 | 4 | 16 | 0.148 | 0.165 |
| 1" | 19.0 | 79.5 | 108.0 | 4 | 16 | 0.216 | 0.241 |
| 1-1/4" | 19.0 | 89.0 | 117.0 | 4 | 16 | 0.254 | 0.284 |
| 1-1/2" | 19.0 | 98.5 | 127.0 | 4 | 16 | 0.295 | 0.329 |
| 2" | 21.0 | 120.5 | 152.0 | 4 | 19 | 0.463 | 0.518 |
| 2-1/2" | 25.0 | 139.5 | 178.0 | 4 | 19 | 0.755 | 0.843 |
| 3" | 27.0 | 152.5 | 191.0 | 4 | 19 | 0.928 | 1.037 |
| 4" | 32.0 | 190.5 | 229.0 | 8 | 19 | 1.501 | 1.676 |
| 5" | 32.0 | 216.0 | 254.0 | 8 | 22 | 1.746 | 1.950 |
| 6" | 35.0 | 241.5 | 279.0 | 8 | 22 | 2.229 | 2.489 |
| 8" | 36.5 | 298.5 | 343.0 | 8 | 22 | 3.410 | 3.809 |
| 10" | 43.0 | 362.0 | 406.0 | 12 | 25 | 7.545 | 8.428 |
| 12" | 43.0 | 432.0 | 483.0 | 12 | 25 | 10.828 | 12.095 |

NOTE: Flange bolt hole patterns meet ANSI B16.5

MINHHUNG SCH80 CPVC Piping Sysyems

## Gasket

### MINH HÙNG  PTFE Gasket

###### MINH HÙNG  PTFE Gasket ANSI B16.5

•inch-lb Unit

39

Detail at	 	     sealing part

h	e

EPDM PTFE

D C

d

•SI Unit

| Size | mm | Weight (kg/pc) | N·m{kgf-cm} |
| --- | --- | --- | --- |
|  | d | D1 | D2 | PCD | D | n-φh |  |  |
| 1/2" | 18 | 30 | – | 60 | 86 | 4-16 | 0.025 | 16{160} |
| 3/4" | 22 | 30 | 42 | 70 | 96 | 4-16 | 0.032 | 16{160} |
| 1" | 29 | 37 | 50 | 79 | 105 | 4-16 | 0.046 | 16{160} |
| 1-1/4" | 38 | 46 | 59 | 89 | 115 | 4-16 | 0.051 | 35{350} |
| 1-1/2" | 43 | 53 | 68 | 98 | 125 | 4-16 | 0.057 | 35{350} |
| 2" | 54 | 64 | 83 | 121 | 150 | 4-19 | 0.063 | 35{350} |
| 2-1/2" | 69 | 81 | 101 | 140 | 175 | 4-19 | 0.084 | 52{520} |
| 3" | 80 | 92 | 112 | 152 | 188 | 4-19 | 0.088 | 52{520} |
| 4" | 103 | 124 | 148 | 190 | 226 | 8-19 | 0.105 | 52{520} |
| 5" | 129 | 150 | 174 | 216 | 252 | 8-22 | 0.130 | 63{630} |
| 6" | 153 | 172 | 196 | 241 | 277 | 8-22 | 0.160 | 63{630} |
| 8" | 200 | 222 | 246 | 298 | 340 | 8-22 | 0.200 | 63{630} |
| 10" | 254 | 276 | 300 | 362 | 404 | 12-25 | 0.290 | 75{750} |
| 12" | 305 | 335 | 365 | 432 | 480 | 12-25 | 0.340 | 75{750} |

MINH HÙNG  EPDM Gasket

MINH HÙNG  EPDM Gasket ANSI B16.5

Detail at

sealing part

d D1 D2 PCD D

- h

•inch-lb Unit

40

•SI Unit

| Size | mm | Weight (kg/pc) | N·m{kgf-cm} |
| --- | --- | --- | --- |
|  | d | D1 | D2 | PCD | D | n-φh |  |  |
| 1/2" | 18 | 30 | – | 60 | 86 | 4-16 | 0.023 | 15{150} |
| 3/4" | 22 | 30 | 42 | 70 | 96 | 4-16 | 0.029 | 15{150} |
| 1" | 29 | 37 | 50 | 79 | 105 | 4-16 | 0.040 | 30{300} |
| 1-1/4" | 38 | 46 | 59 | 89 | 115 | 4-16 | 0.046 | 30{300} |
| 1-1/2" | 43 | 53 | 68 | 98 | 125 | 4-16 | 0.050 | 30{300} |
| 2" | 54 | 64 | 83 | 121 | 150 | 4-19 | 0.055 | 30{300} |
| 2-1/2" | 69 | 81 | 101 | 140 | 175 | 4-19 | 0.075 | 45{450} |
| 3" | 80 | 92 | 112 | 152 | 188 | 4-19 | 0.077 | 45{450} |
| 4" | 103 | 124 | 148 | 190 | 226 | 8-19 | 0.095 | 45{450} |
| 5" | 129 | 150 | 174 | 216 | 252 | 8-22 | 0.115 | 55{550} |
| 6" | 153 | 172 | 196 | 241 | 277 | 8-22 | 0.145 | 55{550} |
| 8" | 200 | 222 | 246 | 298 | 340 | 8-22 | 0.185 | 55{550} |
| 10" | 254 | 276 | 300 | 362 | 404 | 12-25 | 0.250 | 65{650} |
| 12" | 305 | 335 | 365 | 432 | 480 | 12-25 | 0.278 | 65{650} |

MINHHUNG SCH80 CPVC Piping Sysyems

# Engineering Data

  - Pressure Design	43

  - Hydraulic Design	51

  - Water Hammer	59

  - Thermal Linear Expansion and Contraction	61

  - Support Spacing	67

## 1	Pressure Design

##### Maximum Operating Pressure

The maximum operating pressures listed on the right are based on the hydrostatic design of the product using wa- ter as a test medium at 73˚F (23˚C).

The maximum operating pressure can be calculated from the following equations;

43	P = 2σt D-t

where;

P : pressure

D : average outside diameter

t : minimum wall thickness

σ : hydrostatic design stress (HDS)

2,000 psi (13.79MPa) for MINH HÙNG  PVC Type I, Grade 1 2,000 psi (13.79MPa) for MINH HÙNG  CPVC

The following temperature corrections must be used to de-rate all PVC and CPVC pipe, valves and fittings when operating temperatures are expected to exceed 73˚F (23˚C). The working pressure of PVC and CPVC pipe is directly affected by temperature changes. When the operating temperature of the pipe increases, the pipe loses its stiffness and tensile strength decreases. As a result, the maximum operating pressure drop. The drop can be calculated using the chart shown on the next page. Multiply the maximum working pressure by the temperature de-rating factor for the applid temperature on site.

For example, for 2” Schedule 80 PVC pipe, the maximum working pressure is 400 psi (2.76MPa). If the operating temperature is known to be 110˚F (43˚C), the temperature de-rating factor can be found on the chart to be 0.63. The maximum working pressure would be 400 x 0.63 = 252 psi (1.74MPa).

##### Temperature De-rating Factor

inch-lb Unit

1.00

0.90

0.80

0.70

0.60

0.50

0.40

0.30

0.20

0.10

0.00

44

50	100	150	200

Temperature ( F)

Operating Temperature

(°F)	70	80	90	100	110	120	130	140	150	160	170	180	190	200

| PVC SCH80 | 1.00 | 0.90 | 0.81 | 0.72 | 0.63 | 0.55 | 0.47 | 0.39 |  | Not Recommended |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CPVC SCH80 | 1.00 | 0.92 | 0.84 | 0.76 | 0.69 | 0.62 | 0.55 | 0.49 | 0.43 | 0.37 0.31 0.26 | 0.21 0.17 |

S I Unit

1.00

0.90

0.80

0.70

0.60

0.50

0.40

0.30

0.20

0.10

0.00

0

50

Temperature ( C)

100

Operating Temperature

(°C)	20	30	40	50	60	70	80	90

| PVC SCH80 | 1.00 | 0.83 | 0.67 | 0.52 | 0.38 | Not Recommended |
| --- | --- | --- | --- | --- | --- | --- |
| CPVC SCH80 | 1.00 | 0.85 | 0.72 | 0.59 | 0.48 | 0.37 0.27 0.19 |

NOTE:This data should be used as a general recommendation only and not as a guarantee of performance or longevity.

MINHHUNG SCH80 CPVC Piping Sysyems

## 1	Pressure Design

##### Design Pressure/Temperature Relation

PVC

inch-lb Unit	S I Unit

45	1000

900

800

700

600

500

400

300

200

100

0

1/2"

3/4"

1"

1-1/4"

1-1/2"

2"

2-1/2"

3"

4"

5"

6"

8"

24"

8.0

7.0

6.0

5.0

4.0

3.0

2.0

1.0

0.0

1/2"

3/4"

1"

1-1/4"

1-1/2"

2"

2-1/2"

3"

4"

5"

6"

8"

24"

CPVC

inch-lb Unit	S I Unit

1000

900

800

700

600

500

400

300

200

100

0

1/2"

3/4"

1"

1-1/4"

1-1/2"

2"

2-1/2"

3"

4"

5"

6"

8"

24"

50	100	150	200

Temperature (°F)

7.0

6.0

5.0

4.0

3.0

2.0

1.0

0.0

1/2"

1-1/

1-1/

0	20	40	60	80	100

Temperature (°C)

##### Design Tensile Stress

PVC

inch-lb Unit	S I Unit

5000

4000

3000

Estimated Rupture Stress

@105h

50

40	Estimate

@105h

30

46

upture Stress

2000	20

1000

0

Design Stress

=(Estimmaatteedd Rupture Stress)/2

50	100	150	200

Temperature (°F)

10

Design Stress

=(Estimmaatteedd Rupture Stress)/2

0

0	20	40	60	80	100

Temperature (°C)

CPVC

inch-lb Unit	S I Unit

5000

4000

3000

Estimated Rupture Stress

@105h

50

Estimated Rupture Stress

@105h

30

2000	20

1000

Design Stress

=(Estimmaated   Rupture Stress)/2

10

Design Stress

=(Estimateedd Rupture Stress)/2

0

50	100	150	200

Temperature (°F)

0

0	20	40	60	80	100

Temperature (°C)

MINHHUNG SCH80 CPVC Piping Sysyems

## 1	Pressure Design

##### Tensile Strength/Temperature Relation

inch-lb Unit

10000

8000

47

6000

4000

2000

0

50	100	150	200

Temperature (˚F)

S I Unit

60.0

50.0

40.0

30.0

20.0

10.0

0.0

0	50	100

Temperature (˚C)

##### Burst Pressure/Temperature Relation

PVC

inch-lb Unit	S I Unit

3500

3000

2500

2000

1500

1/2"

25.0

20.0

15.0

10.0

1/2"	48

1000

500

5.0

0

50	70	90	110	130	150

Temperature (°F)

0.0

0	20	40	60	80

Temperature (°C)

CPVC

inch-lb Unit	S I Unit

3500

3000

2500

2000

1500

1000

500

1/2"

3/4"

1"

1-1/4"

1-1/2"

2"

2-1/2"

3"

4"

5"

6"

8"

24"

25.0

20.0

15.0

10.0

5.0

1/2"

3/4"

1"

1-1/4"

1-1/2"

2"

2-1/2"

3"

4"

5"

6"

8"

24"

0

50	100	150	200

Temperature (°F)

0.0

0	20	40	60	80	100

Temperature (°C)

MINHHUNG SCH80 CPVC Piping Sysyems

## Pressure Design

##### Long-term Hydrostatic Pressure Performance

PVC

inch-lb Unit

49	10000

73(F)

S I Unit

100

23(°C)

1000	10

100

1

10	100	1000	10000	100000

Time (hrs)

1

1	10

100	1000	10000	100000

Time (hrs)

CPVC

inch-lb Unit	S I Unit

10000

1000

140(F)

176(F)

100

10

100

1	10	100	1000	10000	100000

Time (hrs)

1

1	10	100	1000	10000	100000

Time (hrs)

##### Cyclic Pressure Performance (Fatigue)

inch-lb Unit

10000

50

1000

100

10000	100000	1000000	10000000

Number of Loaded Stress at Break (cycle)

S I Unit

100

10

1

10000	100000	1000000	10000000

Number of Loaded Stress at Break (cycle)

MINHHUNG SCH80 CPVC Piping Sysyems

## Hydraulic Design

Hydraulic Design for Pressure Piping	 For hydraulic design such as flow rate or pressure head loss, Hazen-Williams formula can be used. The friction loss in hydraulic flow can be evaluated through the use of various flow coefficients. One such coef- ficient is the Hazen-Williams C factor. This factor for PVC and CPVC plastic pipe has been set at C = 150. The friction loss can be calculated from the following equation;

inch-lb Unit

51

100 1.852

Q1.852

hf = 0.2083  ·	C

where;

·	di4.8655 · L

hf : friction head loss (ft)

C : constant for inside pipe roughness (C = 150 for PVC and CPVC pipe)

Q : flow rate (U.S. gallon/min)

di : inside diameter (in)

L : pipe length (ft)

S I Unit

100 1.852

Q1.852

hf = 0.2167 ·	C

where;

·	di4.8655 · L

hf : friction head loss (m)

C : constant for inside pipe roughness (C=150 for PVC and CPVC pipe)

Q : flow rate (m3/sec)

di : inside diameter of pipe (m)

L : pipe length (m)

Typical Values of "C" Coefficient

| Pipe Material | C |
| --- | --- |
| Polyvinyl Chloride (PVC) Pipe | 150 |
| Chlorinated polyvinyl Chloride (CPVC) Pipe | 150 |
| Glassfiber Reinforced Plastic Pipe | 140 |
| Highly Smooth Pipes (all metals) | 130-140 |
| Cast Iron (old) | 100 |
| Iron (Worn/pitted) | 60-80 |
| Smooth Masonry | 120 |
| Vitrified Clay | 110 |
| Brick | 100 |

Flow Diagram

inch-lb Unit

10,000

1,000

52

100

10

1

0.1 1	10	100	1,000	10,000

Q : Flow (U.S.Gallons per minute)

S I Unit

1,000

100

10

1

0.1

0.1	1	10	100	1000

Q : Flow (Liters per second)

MINHHUNG SCH80 CPVC Piping Sysyems

## 2	Hydraulic Design

##### Friction Loss Table

inch-lb Unit

53

54

MINHHUNG SCH80 CPVC Piping Sysyems

## 2	Hydraulic Design

##### Friction Loss Table

S I Unit

55

56

MINHHUNG SCH80 CPVC Piping Sysyems

## 2	Hydraulic Design

Friction Loss Through Fittings	 A piping installation consists of pipe, fittings and valves. Normally loss through a fitting is described as being equivalent to loss through a certain number of linear feet of straight pipe.

The friction loss of tee and elbow can be calculated from the following formula;

V2

hf = f · 2g

where;

57	hf : friction head loss (ft, m)

V : water velocities (ft/sec, m/sec)

g : acceleration of gravity (32.15ft/sec2, 9.8m/sec2)

f : fitting loss factor

Fitting Loss Factor

| Fitting Loss Factor | Tee Run | Tee Branch | 90° Elbow | 45° Elbow | Reducing Coupling |
| --- | --- | --- | --- | --- | --- |
| f | 0.35 | 1.2 | 1 | 0.4 | 0.1 ～ 0.5 |

Friction Loss in PVC and CPVC Fittings in Equivalent Length of Straight Pipe

inch-lb Unit	S I Unit

NOTE: The table above is applied at V= 5feet/sec	NOTE: The table above is applied at V= 1.5m/sec

Hydraulic Design for Drainage Flow	 For drainage flow such as open channel flow, Manning formula can be used. The Manning n value, like the Hazen-Williams C factor, is an empirical number that defines the interior wall smoothness of a pipe. The “n” value is 0.01 for PVC and CPVC pipe. The flow rate for drainage pipe can be calculated from the following formula;

Q = A · V

V =	k	·  3 R2 ·	I	Di	58

n	8

where;

Q : flow (ft3/s , m3/s)	 	H

A : cross-sectional area of flow (ft2, m2)

Di2 ( θ– sinθ)

A =	8

Di : Inside diameter of the pipe(ft , m)

θ: angle which the water surface and the center of pipe make. (radian)

V : cross-sectional average velocity (ft/s, m/s)

Range of "n" Values for Various Pipe Materials

| k : 1.486 for Inch-lb units and k = 1.0 for SI units n : manning coefficient of roughness n = 0.01 for PVC and CPVC pipe R : hydraulic radius (ft, m) R = A S | Pipe Material Polyvinyl Chloride (PVC) Pipe Chlorinated polyvinyl Chloride (CPVC) Glassfiber Reinforced Plastic Riveted and Spiral Steel Cast Iron (old) | n 0.01 0.01 0.01 0.013-0.017 0.011-0.015 |
| --- | --- | --- |
| I : slope of pipe (ft/ft, m/m) | Wrought Iron (black) | 0.012-0.015 |
| S : wetted perimeter (ft , m) | Wrought Iron (galvanized) | 0.013-0.017 |

S =

for the full flow

k

Di 2/3

Concrete-Rubble Surface	0.017-0.030

Smooth Brass	0.009-0.013

Vfull =  n   ·	4	·	I

NOTE: For relative roughness (e/D) of PVC pipe, e = 0.000005 ft.

Q	= π · Di2 · V	1

full	4

full

0.9

0.8

0.7

0.6

0.5

0.4

0.3

0.2

0.1

0

0.0

0.2	0.4	0.6	0.8	1.0	1.2	1.4

Q/Qfull, V/Vfull, R/Rfull

MINHHUNG SCH80 CPVC Piping Sysyems

## 3	Water Hammer

Water Hammer Calculation	 When a pipe contains a column of moving liquid, considerable kinetic energy is stored in the liquid by virtue of its mass and velocity. If the velocity is suddenly destroyed by the quick closing of a valve this energy cannot be absorbed because liquid is nearly incompressible. Therefore, an instantaneous shock is created which may represent excessively high pressures. Maximum pressure caused by water-hammer may be calculated with the following formula;

59	Inch-lb Unit

a =	4660

1 + kdi Et

(wave velocity for water in PVC pipe)

Ps = aV

2.31·g

where;

(pressure surge)

Ps : pressure surge (psi)

a : wave velocity (ft/sec)

V : maximum velocity change (ft/sec)

g : acceleration of gravity (32.2 ft/sec2)

k : fluid bulk modulus, 300,000 psi for water

di : pipe inside diameter (inches)

E : modulus of elasticity of the pipe, 420,000 psi for PVC, 360,000 psi for CPVC

t : wall thickness (inches)

S I Unit

a =	1420.4

1 + kdi Et

Ps = aV

102.1·g

where;

Ps : pressure surge (MPa)

a : wave velocity (m/sec)

V : maximum velocity change (m/sec)

g : acceleration of gravity, 9.81m/sec2

k : fluid bulk modulus, 2069MPa for water

di : pipe inside diameter (m)

E : modulus of elasticity of the pipe, 2897MPa for PVC, 2483MPa for CPVC

t : wall thickness (m)

Water-hammer calculated by the above formula for PVC and CPVC Piping is only about 1/3 of steel and cast iron pipe. Water-hammer is a commonly used term for pressure surge in a piping system. One of the major causes of surge is a rapid change in velocity. The maximum safe velocity in a PVC or CPVC piping system depends on the specific details of the system and the operating conditions. In general, 5 feet/sec (1.5 m/sec) is considered to be safe. Higher velocities may be considered where the operating character- istics of valves and pumps are known so that sudden changes in flow velocity can be controlled.

Causes of Water Hammer	 Here are some of the more common causes of pressure surge that should be reviewed when a plastic piping system is being considered.

- Speed of opening or closing of regulating type valves.

- Action of pumps starting or stopping.

- Movement of entrapped air through the system.

- Formation of vacuum and column separation.

60

Preventive Measures	 Understanding the concept of water-hammer and designing the system to minimize it is the best possible preventive measures. A few tips to consider when attempting to reduce the causes of surge in a piping system are:

- Keep fluid velocities under 5 feet per second.

- Check the cycling time of valves to prevent abrupt changes in flow. Both manual and actuated valv- ing should be checked for specific closing times.

- Evaluate flow at pump start-up and during spin-down. Also determine how much air, if any, is intro- duced during pump start-up.

- Use surge control devices and standpipes wisely to give flow storage during surge and to minimize- Water-Hammer column separation. Check valves can be used near pumps to help keep lines full.

- Use properly sized vacuum breaker-air relief valves to control the amount of air that is admitted or exhausted throughout the system.

MINHHUNG SCH80 CPVC Piping Sysyems

## Thermal Linear Expansion and

4	Contraction

Thermal expansion and contraction is fairly common in most piping materials. The coefficient of linear expansion or expansivity for PVC and CPVC pipe is the ratio of the change in pipe length per degree change in temperature.

In the design of a piping system where runs are over 100 ft. in length, remember that PVC and CPVC expand roughly 4.5 to 5 times more than iron or steel. An allowance of about 1/3” of expansion or con- traction should be calculated for every 100 feet of pipe run for each 10 degree change between ambient

installation temperature and maximum operating temperature. The movement or growth in pipe length

61	can be significant in the temperature variation between installation and operation is rather large. However, the resultant stresses generated by movement will be somewhat less for plastics than for steel. This is due to a lower modulus of elasticity for PVC and CPVC pipe in comparison to metallics ; and, over time, some stress relaxation will occur with time.

The graph on page 63 illustrates the relationship between temperature change and growth in pipe length.

Adjustments for Above-Ground Thermal Expansion and Contraction

There are many different types of expansion joints available on the market. Each one is designed to compensate for excessive movement of pipe within the system. Depending on the conditions such as settlement site, pressure and temperature, appropriate expansion and contraction method should be selected.

Wrong expansion and contraction method will result in serious damage on piping system.

Expansion Loop	62

As simple and efficient method for growth control, expansion loop can generally be used. Expansion loop is easily fabricated from pipe and elbows. Their drawbacks are offset space requirements and limitations for large diameter pipe.

Flexible Bend

Flexible bend is available in many configurations. They absorb excessive vibration, allow for multi-direc- tional movement, and correct for mis-alignment or structural shift in the system. Negatives are pressure limitations and resistance to corrosive fluids in the case of 100% metallic bends.

##### Plastic Piston Expansion Joint

Usually a fabricated device constructed by telescoping two pieces of pipe. They will allow for consider- able movement in a linear direction only. For this reason, careful alignment is very necessary for smooth operation. The critical component in this joint is the elastomeric o-ring seal, which must be evaluated for chemical and heat resistance as well as positive sealing characteristics during wear.

##### Bellows and Rubber Expansion Joints

Both of these joints will absorb growth in the system due to thermal changes and will allow for dynamic movement of machinery, support structures, and buildings. Rubber expansion joints will allow for axial, lateral, angular and torsional movement. Both types are installed in-lir and are fairly compact. The manu- facturer of each should be consulted to determine specific design advantages and limitations.

MINHHUNG SCH80 CPVC Piping Sysyems

## Thermal Linear Expansion and

4	Contraction

Expansion or Contraction of PVC and CPVC pipe can be calculated from the following formula;

L = Y · L ·   T

where;

L : length of expansion or contraction

L : pipe length of a straight line

Y : coefficient of thermal

3.0 x 10-5 in/in/˚F for PVC

63	3.4 x 10-5 in/in/˚F for CPVC

T : temperature difference between installation and operation.

inch-lb Unit

0.1

0.09

0.08

0.07

Example;

Lenght of piping is 350 feet (4,200”) of straight line

*Pipe material is CPVC.

Coefficient (Y) is 3.4 x 10-5 (0.000034)

*Pipe is installed at an ambient temperature of 60˚F. Maximum anticipated operating temperature is 140˚F. The difference ( T) is 80˚F.

L = 0.000034 x 4,200 x 80 =11.4"

0.06

0.05

0.04

0.03

0.02

0.01

0

0

20	40	60	80	100	120	140	160	180

Temperature Difference (°F)

S I Unit

7

6

5

4

3

2

1

0

0	10	20

30	40	50

60	70	80	90 100

Temperature Difference (°C)

Fundamentals of Adjusting for Expansion and Contraction of Above-Ground Horizontal Pipe

64

MINHHUNG SCH80 CPVC Piping Sysyems

#### Fundamentals of Adjusting for Expansion and Contraction of Above-Ground Horizontal Pipe

64

MINHHUNG SCH80 CPVC Piping Sysyems

#### Allowance for Underground Contraction

PVC Pipe Snaking Installation Procedure	 Installation and operating temperatures for underground pipelines frequently vary. PVC expands under increasing temperatures and contracts with decreasing temperatures. Allowance for thermal expansion and contraction is easily made by snaking the pipe in the trench. Snaking is recommended for pipe using solvent cemented joints or other rigid couplings 1/2” through 2-1/2” nominal size.

When installation temperature is lower than the operating temperature, install the pipe in straight align-	66

ment and bring the pipe up to operating temperature after the joints are cured but before backfilling. When installation temperature is considerably higher than the operating temperature, the pipe should be installed by “snaking” in the trench.

Recommended offsets and loop lengths for up to 2-1/2” nominal size are shown in the chart below.

For pipe diameters above 2-1/2”, the pipe should be installed in a straight alignment. Before backfilling the trench, the temperature of pipe should be allowed to condition to within 15˚F of the design operating temperature. When large swings in operating temperatures are expected, it may be necessary to consult the factory.

NOTE: Piping must not be buried less than 24” in areas of heavy vehicular or construction equipment traffic. Fatigue of the pipe and joints will occur unless they are encased in a suitable, metal conduit.

For additional information and data, please refer to ASTM specifications D2321, D2774, F645, and F690.

Loop offset in Pipe Snaking Procedure for Underground Contraction

inch-lb Unit

(feet)

S I Unit

(cm)

| Loop Length (feet) | 10˚F | 20˚F | 30˚F | Diff 40˚F | rence T 50˚F | emperature 60˚F 70˚F | 80˚F | 90˚F | 100˚F |  | Loop Length (m) | 10˚C | Diffrence Temperature 20˚C 30˚C 40˚C | 50˚C |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 20 | 3.0 | 3.5 | 4.5 | 5.0 | 6.0 | 6.5 | 7.0 | 7.0 | 8.0 | 8.0 |  | 6 | 9 | 13 | 16 | 18 | 20 |
| 50 | 7.0 | 9.0 | 11.0 | 13.0 | 14.0 | 15.5 | 17.0 | 18.0 | 19.0 | 20.0 |  | 15 | 22 | 31 | 37 | 44 | 50 |
| 100 | 13.0 | 18.0 | 22.0 | 26.0 | 29.0 | 31.5 | 35.0 | 37.0 | 40.0 | 42.0 |  | 30 | 44 | 62 | 76 | 90 | 107 |

OFFSET

PIPE

OFFSET

TRENCH CENTERLINE

LOOP LENGTH

2 LOOP LENGTHS OF PIPE

MINHHUNG SCH80 CPVC Piping Sysyems

## 5	Support Spacing

Support and Spacing requirements for PVC and CPVC pipe,fitting,and valves should be designed into the system to allow for increased temperatures. As temperature increases, the tensile strength of PVC and CPVC decreases, so the pipe and associated fixtures must be well supported.

Horizontal piping systems should be supported on uniform centers which are determined by maximum operating temperatures. The following chart shows the recommended support spacing according to size operating temperatures when the transported liquid has a specific gravity of up to 1.00 with no concen- trated loads. The pipe spacing can be calculated from the following formula;.

67	1

y = 185 ·

wL4 EI

where;

y : deflection or sag (in.,cm)

w : weight per unit length (lb./in.,N/cm)

weight is sum of pipe weight and liquid weight

E : modulus of elasticity at given temperature (lb./in.2,N/cm2)

I : moment of inertia (in.4,cm4)

π(Do4-Di4)

I =	64

Do = Outside diameter of the pipe (in.,cm) Di = Inside diameter of the pipe (in.,cm)

Adjustable clevis, ring, or roll hangers and roll stands with broad support surfaces are best for use with PVC and CPVC pipe. Other suitable types include: pipe clamps, straps, and riser clamps. The broader and flatter the support surfaces, the better. They should be filed smooth, taped, or padded to avoid the possibility of damaging the pipe. Also remove any sharp edges or burrs on the clamps, anchors, or any other supporting equipment that could frequently come in contact with the pipe.

Do not clamp or anchor the pipe so that it is held absolutely rigid or constricted. Some slight axial move- ment is necessary.

For vertical lines, it is recommended that the pipe be banded at intervals determined by the vertical load involved. Riser clamps are best utilized if they are supported on spring hangers. Short risers should in- clude a saddle at the bottom and may require an additional hanger at the top.

All valves and points of concentrated loads such as tees and flanges should have support independent of normal span supports. Metallic or lined valves should be fully supported because of the increased weight. At higher temperatures or when the line is transporting hazardous liquids, it may be economically more practical to use a continuous support system.

When pipe clamps are used, they should not force the pipe and fittings into position. To remedy this, each section of the pipeline should be laid out and all connections, whether solvent cemented, screwed, or flanged should be made while the pipe is held in temporary support. Once the joints have been com- pleted, the final clamping can be done. When correctly installed, a clamp, a holder, or a pipe connection can be loosened or removed without the pipeline shifting position.

Recommended Support Spacing

inch-lb Unit

68

S I Unit

| Nominal Pipe Size | Schedule 80 PVC | Schedule 80 CPVC |
| --- | --- | --- |
|  | 16°C | 27°C | 38°C | 49°C | 60°C | 27°C | 38°C | 49°C | 60°C | 71°C | 82°C | 93°C |
| inch | mm | Recommended Support Spacing (m) | Recommended Support Spacing (m) |
| 1/2” | 21.34 | 1.3 | 1.3 | 1.3 | 1.3 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.1 | 1.1 | 1.1 |
| 3/4” | 26.67 | 1.5 | 1.4 | 1.4 | 1.4 | 1.3 | 1.4 | 1.3 | 1.3 | 1.3 | 1.3 | 1.2 | 1.2 |
| 1” | 33.40 | 1.6 | 1.6 | 1.6 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.4 | 1.4 | 1.4 | 1.3 |
| 1-1/4” | 42.16 | 1.8 | 1.8 | 1.7 | 1.7 | 1.6 | 1.7 | 1.6 | 1.6 | 1.6 | 1.5 | 1.5 | 1.4 |
| 1-1/2” | 48.26 | 1.9 | 1.9 | 1.8 | 1.8 | 1.7 | 1.8 | 1.7 | 1.7 | 1.7 | 1.6 | 1.6 | 1.5 |
| 2” | 60.33 | 2.1 | 2.0 | 2.0 | 2.0 | 1.9 | 2.0 | 1.9 | 1.9 | 1.8 | 1.8 | 1.7 | 1.7 |
| 2-1/2” | 73.03 | 2.3 | 2.3 | 2.2 | 2.2 | 2.1 | 2.2 | 2.1 | 2.1 | 2.0 | 2.0 | 1.9 | 1.9 |
| 3” | 88.90 | 2.5 | 2.5 | 2.4 | 2.4 | 2.3 | 2.3 | 2.3 | 2.3 | 2.2 | 2.1 | 2.1 | 2.0 |
| 4” | 114.30 | 2.8 | 2.7 | 2.7 | 2.6 | 2.5 | 2.6 | 2.6 | 2.5 | 2.4 | 2.4 | 2.3 | 2.2 |
| 5” | 141.30 | 3.0 | 3.0 | 2.9 | 2.9 | 2.7 | 2.8 | 2.8 | 2.7 | 2.7 | 2.6 | 2.5 | 2.4 |
| 6” | 168.28 | 3.3 | 3.2 | 3.2 | 3.1 | 3.0 | 3.1 | 3.0 | 3.0 | 2.9 | 2.8 | 2.7 | 2.7 |
| 8” | 219.08 | 3.7 | 3.6 | 3.5 | 3.5 | 3.3 | 3.5 | 3.4 | 3.3 | 3.2 | 3.2 | 3.1 | 3.0 |
| 10” | 273.05 | 4.1 | 4.0 | 3.9 | 3.8 | 3.7 | 3.8 | 3.7 | 3.7 | 3.6 | 3.5 | 3.4 | 3.3 |
| 12” | 323.85 | 4.4 | 4.3 | 4.2 | 4.1 | 4.0 | 4.1 | 4.1 | 4.0 | 3.9 | 3.8 | 3.7 | 3.6 |
| 14” | 355.60 | 4.6 | 4.5 | 4.4 | 4.3 | 4.2 | 4.3 | 4.3 | 4.2 | 4.1 | 4.0 | 3.8 | 3.7 |
| 16” | 406.40 | 4.9 | 4.8 | 4.7 | 4.6 | 4.5 | 4.6 | 4.5 | 4.4 | 4.3 | 4.2 | 4.1 | 4.0 |
| 18” | 457.20 | 5.2 | 5.1 | 5.0 | 4.9 | 4.7 | 4.9 | 4.8 | 4.7 | 4.6 | 4.5 | 4.3 | 4.2 |
| 20” | 508.00 | 5.5 | 5.4 | 5.3 | 5.2 | 5.0 | 5.1 | 5.0 | 4.9 | 4.8 | 4.7 | 4.6 | 4.4 |
| 24” | 609.60 | 6.0 | 5.9 | 5.7 | 5.6 | 5.4 | 5.6 | 5.5 | 5.4 | 5.3 | 5.1 | 5.0 | 4.8 |

NOTE: This data should be used as a general recommendation only and not as a guarantee of performance or longevity.

*Chart based on spacing for continuous spans and for uninsulated lines conveying fluids of specific gravity up to 1.00.

MINHHUNG SCH80 CPVC Piping Sysyems

## 5	Support Spacing

#### Recommended Pipe Hangers for PVC and CPVC Piping Systems

PIPE RINGS	PIPE ROLLS	STRAPS HOOKS

69

Not Recommend

PIPE CLAMPS	PIPE COVERING	BOLT

NOTE: Clamps used as anchors ~such as U-bolts, etc.), if over-tightened, can produce a point-of-load stress on the pipe. This can result in cracking or premature burst failure. If U-bolts must be used, then a metal (Fig. 19) should be placed between the U-bolt and pipe surface. When anchoring plastic pipe, it is always desirable to spread the load over a wide area of contact.

Installation

- Storage and Handling	71

- General Recommendations	73

- Rules and Guidelines	74

## 1	Storage and Handling

Buyer’s Acceptance of Materials	 The person responsible for receiving the pipe should always carefully inspect as much of the pipe as possible before unloading. The receiver should look for transportation damage such as a shift in the load, tie-down straps overtightened, or signs of rough treatment. LTL (less than truckload) pipe shipments that arrive in a closed trailer should be checked as soon as the trailer is opened. Make sure that the pipe has not been toploaded with metallic piping, crates, machinery or any other objects that might crush or im-

pact the plastic pipe. The ends of the pipe should be visually inspected for cracks, cuts, gouges, or heavy

71	deformations. In some cases, especially for large diameter pipe 4” and above, it would be advisable to inspect the bore of the pipes for internal cracks or splits that may have occurred as a result of loading or transportation. The use of a strong flashlight may be necessary to inspect the inside diameter beyond the ends of the pipe. Any and all damages should be witnessed by the truck driver and clearly noted on the transportation documentation with a copy retained by the receiver. The carrier and MINH HÙNG  should be immediately notified of any damages or missing pipe, or items incorrectly shipped.

Unloading and Handling	 After the pipe has been thoroughly inspected and inventoried, it should be unloaded with reasonable care and effort. The person receiving the pipe must decide the means by which the pipe is unloaded and is re- sponsible for any damages that occur during the unloading process. Never push or drag a palletized load of pipe from a truck bed. Pipe should not come into severe contact with sharp objects such as corners of truck beds, loading docks and buildings, forks on forklift trucks, and rocks or other objects on the ground. Forklift forks must never be inserted into the ends of the pipe as a means of lifting or moving.

Handling and Storing on Site

Incorrect way to load pipes

Incorrect way to off-load

On-site transport

Correct way to load pipes

Correct way to off-load

DO NOT DRAG

NOTE: The impact resistance and flexibility of PVC and especially CPVC pipe are reduced by lower temperature conditions. The impact strength for both types of piping materials will decrease as temperatures approach 32˚F (0˚C) and below. Ex- treme care should be taken when unloading and handling pipe in cold weather. Dropping pipe from a truck or forklift can cause damage. Methods and techniques normally used in warm weather may not be acceptable at the lower temperature range.

Pipe Storage	 Indoor storage of pipe is recommended but may not always be convenient. Therefore, when storing pipe outdoors, choose a flat, dry location that will minimize dirt and foreign matter accumulation in the bore and belled end. Palletized pipe should be stacked with wooden pallet bracings touching each other. Stack height will depend on the pipe diameter, the slope of the terrain, and the weather conditions. As a general precaution, palletized pipe should not be stacked higher that eight feet. This should be deter-

mined and approved by the site engineer or responsible management official. Loose pipe lengths should

be stored in racks or dunnage that will evenly support the pipe to prevent longitudinal sag. If pipe is not 72

well supported, especially in warmer weather, it will become permanently bowed and will be difficult to install. The pipe must be protected from the sun and extreme heat. Protect the pipe by covering it with an opaque tarp, leaving the ends open to allow for air circulation through and around the pipe. When pipe is not protected from the sun, extended exposure to ultraviolet rays will cause discoloration. The amount of time in years necessary to cause this will vary with the geographic location and the orientation of the pipe to the sun.

Outdoor Storage	Indoor Storage

Min 3 feet (1m) Spacing

Shade

Min 3 feet (1m) 75mm minimum width

Ground Level

Fitting Storage	 The person responsible for receiving the fittings should take an accurate count of the incoming order and report any discrepancies to MINH HÙNG  and the carrier. Fittings packaged in damaged boxes should be closely inspected. Store fittings in their original packaging. If they must be removed from their boxes, separate them by material type (PVC vs. CPVC), geometric configuration, and diameter size. Never combine your plastic fitting inventory with metallic materials. Avoid storing fittings near an open flame or source of ex- treme heat.

MINHHUNG SCH80 CPVC Piping Sysyems

## 2	General Recommendations

- Solvent Cement Welding

This method of joining is very simple and reliable if

73	it is followed correctly, but any deviations from the recommended basic steps may reduce the strength and integrity of the joint. The procedures for prepa- ration, insertion, and curing should be followed very carefully.

- Expansion and Contraction

The coefficient of linear expansion of PVC and CPVC pipe is greater than that of metallic piping; therefore, take this factor into consideration when designing and installing a PVC or CPVC piping system.

- Hanging and Supporting

The modulus of elasticity of PVC and CPVC pipe is smaller than that of metal pipes. Maximum work- ing temperature and room temperature should be considered when determining the required support spacing.

- Trench Preparation

When laying PVC and CPVC pipe below the ground, care should be taken to remove all rocks, boards, empty primer and cement cans, brushes, bottles and other debris from the trench. Smaller diameters of pipe should be “snaked” in the trench to allow for expansion and contraction. If solvent cement welding is used for the method of joining, snaking, pressure testing, and pipe movement should not be done until after the joints have been given sufficient time to dry.

- Avoid Bending Pipe

Pipe should not be bent in trenches or in above ground installations. Pipe and joints that are stressed can reduce pressure rating and cause failures.

- Protect Plastic Pipe from Contact with Hard

and Pointed Objects.

Impact resistance is lower than for metals.

Use of compressed air or gas in PVC/CPVC pipe and fittings can result in explosive failures and cause severe injury or death.

- Testing

  - NEVER use compressed air, gas or air-over-wa- ter boosters to pressure test PVC or CPVC piping systems. ONLY hydrostatic pressure testing is to be conducted on PVC and CPVC piping systems. Compressed air or gases can surge to high pres- sures and cause explosive failures that could seri- ously injure personnel.

  - Carefully follow all instructions for hydrostatic pressure testing. Failure to follow these instructions can result in a system failure.

  - Before water-testing a system, always bleed all entrapped air from system. Entrapped air is a ma- jor cause of surge and burst failure in plastic piping systems.

## 3	Rules and Guidelines

#### Solvent Cement Welding Joints

##### Joining Equipment and Material

    - Cutting Tool

Saw & Miter Box or Pipe Cutter (Ratchet Type, Wheel Type)

    - Pipe deburring & beveling tool, file or knife

    - Solvent Cement

PVC cement for PVC materials, CPVC cement for CPVC materials

    - Primer

    - Cleaner

    - Cotton Rag

    - Square

    - Scale

    - Felt-tip Pen

    - Tape Measure

    - Brush

    - Insertion Tool (6” and above)

    - Container (Metal Cans to Hold Cement or Primer)

This flare must be removed with a file or deburring tool, as it will scrape the cement away when pipe is inserted into the fitting.

74

①

③

- Cutting	①②③④

Pipe ends must be cut square.

Check the pipe end with a square to make sure it has been cut squarely.

Note: A diagonal cut reduces bonding area in the most	④

effective and critical part of the joint.

Wheel type cutters are not generally recommended for large diameters since they tend to raise flare at the pipe end.

MINHHUNG SCH80 CPVC Piping Sysyems

## 3	Rules and Guidelines

- Deburring	⑤

All burrs, chips, filings, etc., should be removed from both around the pipe before joining.

Use a knife, deburring tool or a half-round coarse file.

All pipe ends should be beveled from 45 degrees.

Note: Failure to chamfer the edge of the pipe may remove

75	cement from the fitting socket, causing the joint to leak.

- Test Dry Fit of the Joint

Check pipe and fittings for dry fit before cementing. The pipe should be inserted to the fitting easily about 1/3 to 2/3 of the socket depth.

- Depth-Of-Entry Mark	⑧⑨

Measure the socket depth of the fitting and mark this distance on the pipe O.D.

This reference mark can be used when joining to ensure the pipe is completely bottomed into the fitting during assembly.

⑤

  - Inspection, Cleaning	⑥⑦

Visually inspect the inside of the pipe and fitting	⑧

sockets and remove all dirt, grease or moisture with a clean dry rag.

Check pipes and fittings possible damage such as splits or cracks and replace if necessary.

⑨

6. Priming	⑩⑪

⑥	This process is necessary to penetrate and soften both pipe and fitting socket surfaces for cement- ing process.

Apply primer to the surface of the pipe and fitting socket with a natural bristle brush.

Move quickly without hesitation to the cement-

ing procedure while surfaces are still wet with primer.

⑦

⑩	⑬

76

    - Joint Assembly	⑭

⑪

Recommended Brush Size for Primer and Cement Application

| Nominal Pipe Size | 1/2 | 3/4 | 1 | 1-1/4 | 1-1/2 | 2 | 2-1/2 | 3 | 4 | 5 | 6 | 8 | 10 | 12 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Brush Width | 1/2 | 1 | 1 | 1 | 1-1/2 | 1-1/2 | 1-1/2 to 2 | 1-1/2 to 2-1/2 | 2 to 3 | 3 | 3 to 5 | 4 to 6 | 6 to 8 | 6 to 8 |

* Use Only Natural Bristle

7. Application of Solvent Cement	⑫⑬  Apply the solvent cement evenly and quickly around the outside of the pipe at a width a little greater than the depth of the fitting socket while the primer is still wet.

Apply a light coat of cement evenly around the inside of the fitting socket. Avoid puddling.

Apply a second coat of cement to the pipe end.

NOTE: Read all warnings on primer and cement cans.

Work quickly, insert the pipe into the fitting socket bottom with a one-quarter turn to evenly distribute the cement.

Do not continue to rotate the pipe after it has reached the bottom of the fitting socket.

A good joint will have sufficient cement to make a bead all the way around the outside of the fitting hub.

Hold the pipe and fitting together for a minimum of 30 seconds to make sure the pipe does not move or push out of the socket.

⑭

    - Cleanup ⑮

Remove all excess cement from around the pipe and fitting with a dry cotton rag while the cement is still soft.

⑫

⑮

MINHHUNG SCH80 CPVC Piping Sysyems

## 3	Rules and Guidelines

    - Initial Set Time

Initial set time is the necessary time to allow before the joint can be carefully handled.

Initial Set Schedule

| Temperature Range | Pipe Sizes 1/2" to 1-1/4" | Pipe Sizes 1-1/2" to 2" | Pipe Sizes 2-1/2" to 8" | Pipe Sizes 10" to 15" | Pipe Sizes 15"+ |
| --- | --- | --- | --- | --- | --- |
| 60 to 100°F | 2 min | 5 min | 30 min | 2 hrs | 4 hrs |
| 40 to 60°F | 5 min | 10 min | 2 hrs | 8 hrs | 16 hrs |
| 0 to 40°F | 10 min | 15 min | 12 hrs | 24 hrs | 48 hrs |

77

Note: In damp or humid weather allow 50% more set time.

    - Joint cure time

Joint cure time is the necessary time to allow before pressurizing system.

Joint Cure Schedule

inch-lb Unit

| Temperature range during assembly and cure periods | Pipe Sizes 1/2" to 1-1/4" | Pipe Sizes 1-1/2" to 2" | Pipe Sizes 2-1/2" to 8" | Pipe Sizes 10" to 15" | Pipe Sizes 15"+ |
| --- | --- | --- | --- | --- | --- |
|  | up to 150psi | up to 150psi | up to 150psi | up to 100psi | up to 100psi |
| 60 to 100°F | 1 hour | 2 hours | 6 hours | 48 hours | 72 hrs |
| 40 to 60°F | 2 hours | 4hours | 12 hours | 96 hours | 6 days |
| 20 to 40°F | 8 hours | 16 hours | 72 hourrs | 8 days | 14 days |

S I Unit

| Temperature range during assembly and cure periods | Pipe Sizes 1/2" to 1-1/4" | Pipe Sizes 1-1/2" to 2" | Pipe Sizes 2-1/2" to 8" | Pipe Sizes 10" to 15" | Pipe Sizes 15"+ |
| --- | --- | --- | --- | --- | --- |
|  | up to 1MPa | up to 1MPa | up to 1MPa | up to 0.7MPa | up to 0.7MPa |
| 15 to 40°C | 1 hour | 2 hours | 6 hours | 48 hours | 72 hrs |
| 5 to 15°C | 2 hours | 4hours | 12 hours | 96 hours | 6 days |
| - 5 to 5°C | 8 hours | 16 hours | 72 hourrs | 8 days | 14 days |

Note: In damp or humid weather allow 50% more cure time.

Helpful Hints

- Work quickly and carefully.

- Use liberal amounts of fresh cement.

- Do not attempt cementing in the rain or in the presence of moisture.

- Do not cement when the temperature is below 40°F or above 90°F under direct sunlight.

- Do not take shortcuts or bypass recommended steps.

- Consult your cement manufacturer for specific questions or problems

Applicable Specification for Solvent Welding

ASTM D-2564 : Solvent cements for PVC plastic pipe and fitting

ASTM D-2855 : Marking solvent cemented joist with PVC pipe and fitting

ASTM A-493 : Solvent cements for CPVC plastic pipe and fitting

ASTM A-656 : Primers for use in solvent cement joints of PVC plastic pipe and fitting

Hydrostatic Pressure Testing

- The last assembled joint should be fully cured before filling the system with water.

- All valves and air relief mechanisms should be opened at the ends and elevations. The system should be filled slowly, flow velocities should not exceed 1 foot per second. This will prevent surge, water hammer, and air entrapment.

- Water flow should continue until all entrapped air is completely flushed out of every branch of the system. Maintain the 1 ft/s velocity until ev- ery valve is checked. A rapid fluctuation of gauge needle during pressure rise may be an indication that entrapped air still remains in the system. Sys- tems should include the appropriate air relief and vacuum breaker valves to vent air during normal operation after installation. Entrapped air is major cause of surge and burst failure in plastic piping systems.

- After filling the system, do not pressurize un- til the responsible engineer is present to witness the test. All personnel in the vicinity of the system should wear safety glasses and hard hats. High voltage electrical equipment should be shielded from a possible spray.

- The piping system should be pressurized to

125% of its maximum design operating pressure. This pressure must not exceed 1.5 times the working pressure of the lowest rated component in the system, i.e. flanges, unions, thread parts, valves, etc.

- The pressure test should not exceed 1 hour.

This should provide enough time to inspect all

joints for leaks. If leaks are found, pressure must 78

be relieved to repair the leak. The system should then be recharged and retested. Consult the fac- tory if you have any questions concerning these steps. 56

Applicators

Select a suitable pure bristle type paint brush. Use a proper width brush or roller to apply the primer and cement (see chart below). Speedy application of cement is important due to its fast drying characteristics.

IMPORTANT NOTE: A dauber type applicator should only be used on pipe sizes 2” and below. For larger diameter pipe, a brush, swab, or roller must be used.

MINHHUNG SCH80 CPVC Piping Sysyems

## 3	Rules and Guidelines

#### 2 Threaded Connection

##### Selection of Materials

Power Threading Machine

Threading Rachet and Pipe Vise (if hand pipe stock is used)

Pipe Dies designed for plastic

79	Strap Wrench

Teflon* Tape or an approved Teflon Paste Cutting and Deburring Tool

Ring Gauge (L-1)

*Trademark of the EJ DuPont Company

##### Making the Pipe Thread

- Cutting and Deburring

PVC or CPVC pipe should be cut square and smooth for easy and accurate threading. A miter box or similar guide should be used when sawing is done by hand. Burrs should be removed inside and out using a knife or plastic pipe deburring tool.

- Threading

Threading Schedule 80 PVC and CPVC pipe can easily be accomplished using either a standard hand pipe stock or a power operated tool. Cutting dies should be clean and sharp. Power thread- ing machines should be fitted with dies having a 5˚negative front rake and ground especially for plastic pipe. Self-opening die heads, and a slight chamfer to lead the dies will speed the operation; however, dies should not be driven at high speeds or with heavy pressure. When using a hand held cutter, the pipe should be held in a pipe vise. To prevent crushing or scoring of the pipe by the vice jaws, some type of protective wrap such as canvas, emery paper, rubber, or light metal sleeve should be used. For hand stocks, the dies should

have a negative front rake angle of 5˚ to 10˚ PVC and CPVC is readily threaded and caution should be taken not to over-thread.

- Preparing the Threaded Pipe

A ring gauge should be used to check the ac- curacy of the threads. Tolerance = ± 1-1/2 turns. The threads should then be cleaned by brushing away cuttings and ribbons.

After cleaning, apply a thread lubricant such as Teflon tape to the threaded portion of pipe. Wrap the tape around the entire length of threads be- ginning with number two thread from the end. The tape should slightly overlap itself going in the same direction as the threads. This will pre- vent the tape from unraveling when the fitting is tightened on the pipe. Overlapping in the wrong direction and the use of too much tape can affect tolerances between threads. This can generate stress in the wall of female fittings resulting in fail- ure during operations.

- Assembly of Threaded Joints

After applying thread lubricant, screw the thread- ed fitting onto the pipe. Screwed fittings should be started carefully and hand tightened. Threads must be properly cut and a good quality thread lubricant/tape must be used. If desired, the joint may be tightened with a strap wrench. IN NO CASE SHOULD A STILLSON TYPE WRENCH

BE USED. The jaws of this type of wrench will scar and damage the pipe wall. Fittings should be threaded together until hand tight with an ad- ditional 1 to 1-1/2 turns more. Avoid stretching or distorting the pipe, fittings or threads by over tightening.

NOTE:

(1.) Never apply solvent cement to threaded pipe or threaded fittings. Do not allow cleaners, primers, or sol- vent cements to “run” or drip into the threaded portion of the fitting.

(2.) Some Teflon pastes contain chemicals that may be harmful to the pipe and fittings. You should consult the supplier or manufacturer of the paste before use.

(3.) Avoid screwing metallic’ male threads into plastic female threads. If connections to metal threads have to be made, the preferred method is to screw a plastic male

thread into a metallic female thread. There are a variety

of plastic fittings that are molded with metallic male or 80

female NPT threaded inserts. The corrosion resistance of the metal insert will have to be taken into consideration. Consult the factory or your MINH HÙNG  sales person for the availability of these metal insert fittings.

*Trademark of the E.I. DuPont Company.

##### ANSI B1.20.1 Taper Pipe Thread Dimensions

B

A

C

60˚	E	D

60˚

MINHHUNG SCH80 CPVC Piping Sysyems

## 3	Rules and Guidelines

#### 3 Flange Connection

- Selection of Materials	 MINH HÙNG  Gasket must be resistant to chemicals flowing through the line.

Fasteners-bolts, nuts, and washers, also resistant to the chemical environment. (Threads should be

81	well lubricated.)

Torque Wrench-a necessity for tightening bolts in a manner that guards against excessive torque.

- Flange Assembly

  - Join the flange to the pipe as outlined in the solvent cementing section or in the threading sec- tion depending on the joining method desired.

  - Align the flanges and gasket by inserting all of the bolts through the matching bolt holes. Proper mating of flanges and gaskets is very important for a positive seal.

  - Using a torque wrench, tighten each bolt in

a gradual sequence as outlined by the flange sketch. For final tightening of all bolts, find the recommended torque value in the chart below.

Recommended Torque

12-Bolt

⑫	①

8-Bolt	⑧	⑧

4-Bolt ④ ④ ④

①	⑤

① ⑤ ⑨

⑩ ⑥  ②	③ ③ ③

⑥	②	⑦	⑦

②	⑪

Bolt lengths were calculated using two Eaton flanges. Additional accessories or different mating surfaces will alter these numbers

NOTE: Flange bolt hole pattern meets ANSI B16.5

# Chemical Resistance

## Chemical Resistance

- Chemical Resistance Material Composed MINH HÙNG  Pipes, Fittings and vales

83

- Explanation of Chemical Resistance Guide

| Mark | Chemical Resistance |
| --- | --- |
| ++ | Excellent Resistant |
| + | Good Resistant |
| – | Conditionally Resistant |
| – – | Not Recommended |

*Cautionary Note Regarding The Chemical Resistance Guide

This table is intended to serve as a guide only. The information based on data accumulated from immersion test and experiments herein is believed to be reliable, but no repesentations, guarantee or warranties of any kinds are made as to its accuracy, suitability for paticular applications or results to be obtained.

Before actual permanet installation, the final decision regarding material suitability must be based on in-service testing. We are providing the consultation service based on your specific use condition.

84

MINHHUNG SCH80 CPVC Piping Sysyems

## Chemical Resistance

85

86

MINHHUNG SCH80 CPVC Piping Sysyems

## Chemical Resistance

87

88

MINHHUNG SCH80 CPVC Piping Sysyems

## Chemical Resistance

89

90

MINHHUNG SCH80 CPVC Piping Sysyems

## Chemical Resistance

91

92

MINHHUNG SCH80 CPVC Piping Sysyems

## Chemical Resistance

93

94

MINHHUNG SCH80 CPVC Piping Sysyems

## Chemical Resistance

95

96

MINHHUNG SCH80 CPVC Piping Sysyems

## Chemical Resistance

97

98

MINHHUNG SCH80 CPVC Piping Sysyems

## Chemical Resistance

99

MINHHUNG SCH80 CPVC Piping Sysyems

100

## Chemical Resistance

101

MINHHUNG SCH80 CPVC Piping Sysyems

102

## Chemical Resistance

103

MINHHUNG SCH80 CPVC Piping Sysyems

104

## Chemical Resistance

105

MINHHUNG SCH80 CPVC Piping Sysyems

106

Cpvc pipe & fitting system

# Safety Precautions

## Safety Precautions

109

PVC and CPVC plastic piping systems will give excellent, maintenance-free performance over many years use,as long as the application and system design is correct and installation is prop- erly done. It is most important to know the physi- cal properties and limitations of PVC and CPVC plastic pipe when selecting these materials for an application and when designing the system. In every case, carefully read and follow installa- tion procedures. It is very important to know the reputation and abilities of your installation crew or contractor. Professional engineering design of the system and close supervision of the assembly- installation procedures are highly recommended. Any questions concerning the application or in- stallation of PVC and CPVC piping products should be directed to the supplier, manufacturer or consultant.

General

- Protect plastic pipe from contact with hard and pointed objects

Impact resistance is lower than for metals.

- Avoid bending pipe

Pipe should not be bent in trenches or in above ground installations. Pipe and joints that are stressed reduce pressure rating and can cause failures.

- Protect pipe from extreme heat and cold.

Extremes of heat and cold can cause failure. Al- lowing liquids to freeze inside PVC/CPVC and metallic piping can cause the pipe and/or the joints to crack. Freeze protection should be de-

signed into the system. Heat beyond design lim- its can also cause failures.

- Protect pipe from sunlight.

PVC and CPVC pipe compounds normally do not provide extended protection from the ultraviolet rays of the sun. Therefore, unless the material has been specially formulated to provide protection, the product must be protected from sunlight or some damage may occur after years of expo- sure.

##### Application

- NEVER use PVC and CPVC piping materials to transport compressed air or gases. Compressed air or gases can surge to high pres- sures and cause explosive failures that could seri- ously injure personnel. PVC and CPVC pipe and fittings are excellent products in transporting wa- ter and corrosive chemicals.

- Only use approved chemicals.

Certain chemicals, especially petroleum distillates and derivatives, can cause failure. Every chemical should be verified and approved in the manufac- turer's chemical resistance chart.

##### System Design

- Allow for flexibility in the design of the system. Expansion and contraction is greater than for metals. This can cause breaks and leaking points if system design is not flexible to allow for move- ment. When laying smaller diameters of pipe be- low ground, the pipe should be "snaked" in the trench to allow for expansion and contraction. If solvent cement welding is used for the method of joining, snaking, pressure testing, and pipe movement should not be done until after the joints have been given sufficient time to dry.

- Design safeguards into the system to prevent excessive surge pressures.

Water hammer (surge) in a PVC and CPVC sys- tem can cause pipe, fittings, and valves to burst. Liquid velocities should not exceed five feet per second maximum.

##### Installation

- Carefully follow solvent cement welding in- structions.

Failure to correctly follow application procedures can reduce the strength and integrity of joints and cause joint failures. By far, the majority of failures in PVC and CPVC systems are the result of short- cuts and/or improper joining techniques.

- Remove rocks and other debris that can rup-

ture pipe when burying pipe in trenches.

When laying PVC and CPVC pipe below the ground, care should be taken to remove all rocks, boards, empty primer and cement cans, brushes, bottles and other debris from the trench. Backfill- ing and top loading should be watched very care- fully.

- Follow recommended support spacing for

PVC and CPVC piping systems.

The modulus of elasticity of PVC and CPVC pipe is smaller than metals. Maximum working tem- perature and room temperature should be con- sidered when determining the required support spacing.

##### Testing

- NEVER use compressed air or gas or air-over- water boosters to pressure test PVC or CPVC piping systems.

ONLY hydrostatic pressure testing is to be con- ducted on PVC and CPVC piping systems. Com-

pressed air or gases can surge to high pressures and cause explosive failures that could seriously injure personnel.

- Carefully follow all instructions for hydrostatic

pressure testing.

Failure to follow these instructions can result in a system failure.

- Before water-testing a system, always bleed

all entrapped air from system.

Entrapped air is a major cause of surge and burst failure in plastic piping systems.

110

MINHHUNG SCH80 CPVC Piping Sysyems

# MINH HUNG PLASTICS JOINT STOCK COMPANY

103/7 Ao Doi Str., Binh Tri Dong A Ward, Binh Tan Dist., HCM City
Telephone:(+84 8) 3875 5448 - (+84 8) 3750 5381
Fax: (+84 8) 37504087 | Email: info@minhhungplast.com.vn

Copyright  2017

TC VIETNAM GLOBAL CO., LTD.

SCH80 PVC & CPVC Piping Systems Speciﬁcations & Engineering Manual

VN GLOBAL TC LIMITED COMPANY

DISTRIBUTOR OF MINHHUNG IN VIETNAM

124 Phuc Dien, Cau Giay Dist, Ha Noi City

Telephone/fax: 024. 32272046 |  Email: tuannq@tctoancau.com | Web: www.tctoancau.com

Facebook: https://facebook.com/nhuaminhungmienbac/

# Text boxes

!

! DANGER

! WARNING

! CAUTION

1

Advantages of Eslon Sch80 PVC and CPVC Pipe

Advantages of Eslon Sch80 PVC and CPVC Pipe

2

| ITEM | Test Method | inch-lb unit |
| --- | --- | --- |
|  |  | unit | PVC | CPVC |
| GENERAL |
| Cell Classification | ASTM D1784 | — | 12454 | 23447 |
| Maximum Usable Temp. | — | °F | 140 | 200 |
| Specific Gravity @ 73°F(23°C) | ASTM D792 | g/cc | 1.42±0.02 | 1.55±0.02 |
| Water Absorption % increase 24 hrs@ 73°F(23°C) | ASTM D570 | ％ | 0.04 | 0.04 |
| Hardness, Rockwell | ASTM D785 | — | 110 - 120 | 115-125 |
| Poisson’s Ratio @ 73°F(23°C) | ASTM D638 | — | 0.38 | 0.36 |
| MECHANICAL |
| Tensile Strength @ 73°F(23°C) | ASTM D638 | psi | 7,100 | 7,700 |
| Tensile Strength @194 °F(90°C) | 〃 | psi | — | 3,200 |
| Tensile Modulus of Elasticity @ 73°F(23°C) | 〃 | psi | 410,000 | 380,000 |
| Tensile Modulus of Elasticity @ 194°F(90°C) | 〃 | psi | — | 220,000 |
| Flexural Strength @ 73°F(23°C) | ASTM D790 | psi | 14,000 | 13,000 |
| Flexural Modulus of Elasticity @ 73°F(23°C) | 〃 | psi | 400,000 | 390,000 |
| Compressive Strength @ 73°F(23°C)ε =10％ | ASTM D695 | psi | 10,000 | 14,000 |
| Compressive Modulus of Elasticity @ 73°F | 〃 | psi | 110,000 | 145,000 |
| Izod Impact, notched @ 73°F(23°C) | ASTM D256 | ft-lb/in | 1.5 | 3.0 |
| THERMAL |
| Coefficient of Linear Expansion | ASTM D696 | in/in/°F | 2.5-3.5x10 -5 | 3.0-4.0x10 -5 |
| Coefficient of Thermal Conductivity | ASTM C177 | BTU/in/hr/ft.2/°F | 1.20 | 0.90 |
| Heat Deflection Temperature Under Load (264psi, annealed) | ASTM D648 | °F | 165 | 230 |
| Specific Heat | ASTM D2766 | Cal./°C/g | 0.27 | 0.26 |
| ELECTRICAL |
| Volume Resistivity | ASTM D257 | ohm/cm | >1.0 x 10 15 | >1.0 x 10 15 |
| Dielectric Strength | ASTM D149 | volt/mm | >1000 | >1000 |
| Dielectric Constant | ASTM D150 | — | 3 | 3 |
| Power Factor | 〃 | — | 0.01-0.02 | 0.01-0.02 |
| Electrical Conductivity | — | — | Non Conductor | Non Conductor |
| FIRE PERFORMANCE |
| Flammability Rating | UL-94 | — | -0 | V-0, 5VB, 5VA |
| Flame Spread Index | 〃 | — | <10 | <10 |
| Average Time of Burning | ASTM D635 | sec | <5 | <5 |
| Average Extent of Burning | 〃 | mm | <10 | <10 |
| Burning Rate | 〃 | mm/min | Self Extinguishing | Self Extinguishing |
| Limiting Oxygen Index (LOI) | ASTM D2863 | LOI | 45 | 60 |

Ống và phụ kiện CPVC Sch80

| ITEM | Test Method | SI unit |
| --- | --- | --- |
|  |  | unit | PVC | CPVC |
| GENERAL |
| Cell Classification | ASTM D1784 | — | 12454 | 23447 |
| Maximum Usable Temp. | — | °C | 60 | 93 |
| Specific Gravity @ 73°F(23°C) | ASTM D792 | g/cc | 1.42±0.02 | 1.55±0.02 |
| Water Absorption % increase 24 hrs@ 73°F(23°C) | ASTM D570 | ％ | 0.04 | 0.04 |
| Hardness, Rockwell | ASTM D785 | — | 110 - 120 | 115-125 |
| Poisson’s Ratio @ 73°F(23°C) | ASTM D638 | — | 0.38 | 0.36 |
| MECHANICAL |
| Tensile Strength @ 73°F(23°C) | ASTM D638 | MPa | 49.0 | 53.1 |
| Tensile Strength @194 °F(90°C) | 〃 | MPa | — | 22.1 |
| Tensile Modulus of Elasticity @ 73°F(23°C) | 〃 | GPa | 2.83 | 2.62 |
| Tensile Modulus of Elasticity @ 194°F(90°C) | 〃 | GPa | — | 1.52 |
| Flexural Strength @ 73°F(23°C) | ASTM D790 | MPa | 96.5 | 89.6 |
| Flexural Modulus of Elasticity @ 73°F(23°C) | 〃 | GPa | 2.76 | 2.69 |
| Compressive Strength @ 73°F(23°C)ε =10％ | ASTM D695 | MPa | 69.0 | 96.5 |
| Compressive Modulus of Elasticity @ 73°F | 〃 | GPa | 0.76 | 1.00 |
| Izod Impact, notched @ 73°F(23°C) | ASTM D256 | J/m | 80 | 160 |
| THERMAL |
| Coefficient of Linear Expansion | ASTM D696 | m/m/°C | 6.0-8.0x10 -5 | 7.0-8.0x10 -5 |
| Coefficient of Thermal Conductivity | ASTM C177 | Watt/m/°K | 0.17 | 0.13 |
| Heat Deflection Temperature Under Load (264psi, annealed) | ASTM D648 | °C | 74 | 110 |
| Specific Heat | ASTM D2766 | J/°K/g | 1.1 | 1.1 |
| ELECTRICAL |
| Volume Resistivity | ASTM D257 | ohm/cm | >1.0 x 10 15 | >1.0 x 10 15 |
| Dielectric Strength | ASTM D149 | volt/mm | >1000 | >1000 |
| Dielectric Constant | ASTM D150 | — | 3 | 3 |
| Power Factor | 〃 | — | 0.01-0.02 | 0.01-0.02 |
| Electrical Conductivity | — | — | Non Conductor | Non Conductor |
| FIRE PERFORMANCE |
| Flammability Rating | UL-94 | — | V-0 | V-0, 5VB, 5VA |
| Flame Spread Index | 〃 | — | <10 | <10 |
| Average Time of Burning | ASTM D635 | sec | <5 | <5 |
| Average Extent of Burning | 〃 | mm | <10 | <10 |
| Burning Rate | 〃 | mm/min | Self Extinguishing | Self Extinguishing |
| Limiting Oxygen Index (LOI) | ASTM D2863 | LOI | 45 | 60 |

Eslon Sch80 PVC and CPVC Pipe and Fittings

| ITEM | Test Method | inch-lb unit |
| --- | --- | --- |
|  |  | unit | PVC | CPVC |
| GENERAL |
| Cell Classification | ASTM D1784 | － | 12454 | 23447 |
| Maximum Usable Temp. | － | °F | 140 | 200 |
| Specific Gravity @ 73°F 23°C | ASTM D792 | g/cc | 1.42±0.02 | 1.55±0.02 |
| Water Absorption % increase 24 hrs@ 73°F 23°C | ASTM D570 | ％ | 0.04 | 0.04 |
| Hardness, Rockwell | ASTM D785 | － | 110 - 120 | 115-125 |
| Poisson's Ratio @ 73°F 23°C | ASTM D638 | － | 0.38 | 0.36 |
| MECHANICAL |
| Tensile Strength @ 73°F 23°C | ASTM D638 | psi | 7,700 | 7,700 |
| Tensile Strength @194 °F 90°C | 〃 | psi | － | 3,200 |
| Tensile Modulus of Elasticity @ 73°F 23°C | 〃 | psi | 420,000 | 380,000 |
| Tensile Modulus of Elasticity @ 194°F 90°C | 〃 | psi | － | 220,000 |
| Flexural Strength @ 73°F 23°C | ASTM D790 | psi | 13,000 | 13,000 |
| Flexural Modulus of Elasticity @ 73°F 23°C | 〃 | psi | 420,000 | 390,000 |
| Compressive Strength @ 73°F 23°C =10 | ASTM D695 | psi | 10,000 | 14,000 |
| Compressive Modulus of Elasticity @ 73°F | 〃 | psi | 110,000 | 145,000 |
| Izod Impact, notched @ 73°F 23°C | ASTM D256 | ft-lb/in | 1.0 | 3.0 |
| ELECTRICAL |
| Coefficient of Linear Expansion | ASTM D696 | in/in/°F | 2.5-3.5x10 -5 | 3.0-4.0x10 -5 |
| Coefficient of Thermal Conductivity | ASTM C177 | BTU/in/hr/ft.2/°F | 1.11 | 0.90 |
| Heat Deflection Temperature Under Load (264psi, annealed) | ASTM D648 | °F | 170 | 230 |
| Specific Heat | ASTM D2766 | Cal./°C/g | 0.27 | 0.26 |
| ELECTRICAL |
| Volume Resistivity | ASTM D257 | ohm/cm | >1.0 x 10 15 | >1.0 x 10 15 |
| Dielectric Strength | ASTM D149 | volt/mm | >1000 | >1000 |
| Dielectric Constant | ASTM D150 | － | 3 | 3 |
| Power Factor | 〃 | － | 0.01-0.02 | 0.01-0.02 |
| Electrical Conductivity | － | － | Non Conductor | Non Conductor |
| FIRE PERFORMANCE |
| Flammability Rating | UL-94 | － | V-0 | V-0, 5VB, 5VA |
| Flame Spread Index | 〃 | － | <10 | <10 |
| Average Time of Burning | ASTM D635 | sec | <5 | <5 |
| Average Extent of Burning | 〃 | mm | <10 | <10 |
| Burning Rate | 〃 | mm/min | Self Extinguishing | Self Extinguishing |
| Limiting Oxygen Index (LOI) | ASTM D2863 | LOI | 45 | 60 |

Eslon Sch80 PVC and CPVC Pipe and Fittings

| ITEM | Test Method | SI unit |
| --- | --- | --- |
|  |  | unit | PVC | CPVC |
| GENERAL |
| Cell Classification | ASTM D1784 |  | 12454 | 23447 |
| Maximum Usable Temp. |  | °C | 60 | 93 |
| Specific Gravity @ 73°F 23°C | ASTM D792 | g/cc | 1.42±0.02 | 1.55±0.02 |
| Water Absorption % increase 24 hrs@ 73°F 23°C | ASTM D570 | ％ | 0.04 | 0.04 |
| Hardness, Rockwell | ASTM D785 |  | 110 - 120 | 115-125 |
| Poisson's Ratio @ 73°F 23°C | ASTM D638 |  | 0.38 | 0.36 |
| MECHANICAL |
| Tensile Strength @ 73°F 23°C | ASTM D638 | MPa | 53.1 | 51.0 |
| Tensile Strength @194 °F 90°C |  | MPa |  | 20.7 |
| Tensile Modulus of Elasticity @ 73°F 23°C |  | GPa | 2.90 | 2.62 |
| Tensile Modulus of Elasticity @ 194°F 90°C |  | GPa |  | 1.38 |
| Flexural Strength @ 73°F 23°C | ASTM D790 | MPa | 89.6 | 82.7 |
| Flexural Modulus of Elasticity @ 73°F 23°C |  | GPa | 2.90 | 2.76 |
| Compressive Strength @ 73°F (23°C) ε =10％ | ASTM D695 | MPa | 69.0 | 103.4 |
| Compressive Modulus of Elasticity @ 73°F |  | GPa | 0.76 | 1.10 |
| Izod Impact, notched @ 73°F 23°C | ASTM D256 | J/m | 53 | 144 |
| THERMAL |
| Coefficient of Linear Expansion | ASTM D696 | m/m/°C | 6.0-8.0x10 -5 | 7.0-8.0x10 -5 |
| Coefficient of Thermal Conductivity | ASTM C177 | Watt/m/°K | 0.16 | 0.13 |
| Heat Deflection Temperature Under Load (264psi, annealed) | ASTM D648 | °C | 77 | 104 |
| Specific Heat | ASTM D2766 | J/°K/g | 1.1 | 1.1 |
| ELECTRICAL |
| Volume Resistivity | ASTM D257 | ohm/cm | >1.0 x 10 15 | >1.0 x 10 15 |
| Dielectric Strength | ASTM D149 | volt/mm | >1000 | >1000 |
| Dielectric Constant | ASTM D150 |  | 3 | 3 |
| Power Factor | 〃 |  | 0.01-0.02 | 0.01-0.02 |
| Electrical Conductivity |  |  | Non Conductor | Non Conductor |
| FIRE PERFORMANCE |
| Flammability Rating | UL-94 |  | V-0 | V-0, 5VB, 5VA |
| Flame Spread Index | 〃 |  | <10 | <10 |
| Average Time of Burning | ASTM D635 | sec | <5 | <5 |
| Average Extent of Burning |  | mm | <10 | <10 |
| Burning Rate |  | mm/min | Self Extinguishing | Self Extinguishing |
| Limiting Oxygen Index (LOI) | ASTM D2863 | LOI | 45 | 60 |

Eslon Sch80 PVC and CPVC Pipe and Fittings

| Type | Material (Cell Classification) | Dimensions | Commercial Classification |
| --- | --- | --- | --- |
| PVC Schedule 80 | ASTM D-1784 (12454) | ASTM D-1785 | TypeⅠ,Grade 1, PVC 1120 |
| CPVC Schedule 80 | ASTM D-1784 (23447) | ASTM F-441 | Type Ⅳ ,Grade 1, CPVC 4120 |

Eslon Sch80 PVC and CPVC Pipe and Fittings

Eslon Sch80 PVC and CPVC Pipe and Fittings

| Type | Material (Cell Classification) | Dimensions | Commercial Classification |
| --- | --- | --- | --- |
| PVC Schedule 80 | Socket-type | ASTM D-1784 (12454) | ASTM D-2467 | TypeⅠ,Grade 1, PVC 1120 |
|  | Threaded-type |  | ASTM D-2464 |  |
| CPVC Schedule 80 | Socket-type | ASTM D-1784 (23447) | ASTM F-439 | Type Ⅳ ,Grade 1, CPVC 4120 |
|  | Threaded-type |  | ASTM F-437 |  |

Eslon Sch80 PVC and CPVC Pipe and Fittings

d2

d1

OD

d1

d

d

d2

| Nomi- nal Pipe Size | OD inch | Inside Diameter min d inch | Socket Entrance Diameter d1 inch | Socket Bottom Diameter d2 inch | Socket Length min l inch |
| --- | --- | --- | --- | --- | --- |
| 1/2” | 1.181 | 0.630 | 0.848 | ±0.004 | 0.836 | ±0.004 | 0.875 |
| 3/4” | 1.378 | 0.866 | 1.058 | ±0.004 | 1.046 | ±0.004 | 1.000 |
| 1” | 1.693 | 1.063 | 1.325 | ±0.005 | 1.310 | ±0.005 | 1.125 |
| 1-1/4” | 2.087 | 1.457 | 1.670 | ±0.005 | 1.655 | ±0.005 | 1.250 |
| 1-1/2” | 2.362 | 1.654 | 1.912 | ±0.006 | 1.894 | ±0.006 | 1.375 |
| 2” | 2.874 | 2.126 | 2.387 | ±0.006 | 2.369 | ±0.006 | 1.500 |
| 2-1/2” | 3.465 | 2.598 | 2.889 | ±0.007 | 2.868 | ±0.007 | 1.750 |
| 3” | 4.213 | 3.228 | 3.516 | ±0.008 | 3.492 | ±0.008 | 1.875 |
| 4” | 5.236 | 4.094 | 4.016 | ±0.009 | 4.491 | ±0.009 | 2.250 |
| 5” | 6.378 | 5.197 | 5.583 | ±0.010 | 5.553 | ±0.010 | 2.638 |
| 6” | 7.559 | 6.142 | 6.647 | ±0.011 | 6.614 | ±0.011 | 3.031 |
| 8” | 9.724 | 8.268 | 8.655 | ±0.015 | 8.610 | ±0.015 | 4.016 |
| 10” | 12.087 | 10.433 | 10.780 | ±0.015 | 10.735 | ±0.015 | 5.512 |
| 12” | 14.291 | 12.402 | 12.780 | ±0.015 | 12.735 | ±0.015 | 6.102 |
| 14” | 15.512 | 12.410 | 14.035 | ±0.015 | 13.985 | ±0.015 | 9.000 |
| 16” | 17.717 | 14.210 | 16.045 | ±0.015 | 15.980 | ±0.015 | 10.000 |

| Nomi- nal Pipe Size | OD mm | Inside Diameter min d mm | Socket Entrance Diameter d1 mm | Socket Bottom Diameter d2 mm | Socket Length min l mm |
| --- | --- | --- | --- | --- | --- |
| 1/2” | 30 | 16 | 21.54 | ±0.10 | 21.23 | ±0.10 | 22.22 |
| 3/4” | 35 | 22 | 26.87 | ±0.10 | 26.57 | ±0.10 | 25.40 |
| 1” | 43 | 27 | 33.65 | ±0.13 | 33.27 | ±0.13 | 28.58 |
| 1-1/4” | 53 | 37 | 42.42 | ±0.13 | 42.04 | ±0.13 | 31.75 |
| 1-1/2” | 60 | 42 | 48.56 | ±0.15 | 48.11 | ±0.15 | 34.93 |
| 2” | 73 | 54 | 60.63 | ±0.15 | 60.17 | ±0.15 | 38.10 |
| 2-1/2” | 88 | 66 | 73.38 | ±0.18 | 72.85 | ±0.18 | 44.45 |
| 3” | 107 | 82 | 89.31 | ±0.20 | 88.70 | ±0.20 | 47.63 |
| 4” | 133 | 104 | 114.76 | ±0.23 | 114.10 | ±0.23 | 57.15 |
| 5” | 162 | 132 | 141.81 | ±0.25 | 141.00 | ±0.25 | 67.00 |
| 6” | 192 | 156 | 168.83 | ±0.28 | 168.00 | ±0.28 | 77.00 |
| 8” | 247 | 210 | 219.84 | ±0.38 | 218.70 | ±0.38 | 102.00 |
| 10” | 307 | 265 | 273.81 | ±0.38 | 272.67 | ±0.38 | 140.00 |
| 12” | 363 | 315 | 324.61 | ±0.38 | 323.47 | ±0.38 | 155.00 |
| 14” | 394 | 315 | 356.49 | ±0.380 | 355.22 | ±0.38 | 228.60 |
| 16” | 450 | 361 | 410.08 | ±0.380 | 405.89 | ±0.38 | 254.00 |

Ống và phụ kiện CPVC Sch80

| Nominal Pipe Size | inch Pipe O.D. (D) | Female Thread Min. Length (T) | Male Thread Min. Length (S) | Overall Pipe Thread Length (L) | Pitch of Thread (P) | Threads Per In. | Height of Thread |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1/2” | 0.840 | 0.91 | 0.73 | 0.782 | 0.071 | 14.0 | 0.057 |
| 3/4” | 1.050 | 1.02 | 0.73 | 0.794 | 0.071 | 14.0 | 0.057 |
| 1” | 1.315 | 1.14 | 0.83 | 0.985 | 0.087 | 11.5 | 0.070 |
| 1-1/4” | 1.660 | 1.26 | 0.96 | 1.009 | 0.087 | 11.5 | 0.070 |
| 1-1/2” | 1.900 | 1.38 | 0.96 | 1.025 | 0.087 | 11.5 | 0.070 |
| 2” | 2.375 | 1.57 | 1.06 | 1.058 | 0.087 | 11.5 | 0.070 |
| 2-1/2” | 2.875 | 1.77 | 1.57 | 1.571 | 0.125 | 8.0 | 0.100 |
| 3” | 3.500 | 1.89 | 1.65 | 1.634 | 0.125 | 8.0 | 0.100 |
| 4” | 4.500 | 2.28 | 1.75 | 1.734 | 0.125 | 8.0 | 0.100 |

Coupling S

X

Eslon Sch80 PVC and CPVC Pipe and Fittings

L

Coupling FT

X

FT

| Size | Inch | Weight (lb/pc) |
| --- | --- | --- |
|  | L | N | PVC | CPVC |
| 1/2” | 1.969 | 0.220 | 0.08 | 0.08 |
| 3/4” | 2.205 | 0.205 | 0.11 | 0.12 |
| 1” | 2.480 | 0.230 | 0.16 | 0.18 |
| 1-1/4” | 2.717 | 0.217 | 0.26 | 0.28 |
| 1-1/2” | 2.953 | 0.202 | 0.36 | 0.39 |
| 2” | 3.346 | 0.346 | 0.55 | 0.60 |
| 2-1/2” | 3.780 | 0.280 | 0.85 | 0.93 |
| 3” | 4.016 | 0.265 | 1.29 | 1.41 |
| 4” | 4.843 | 0.343 | 2.00 | 2.18 |

| Size | mm | Weight (kg/pc) |
| --- | --- | --- |
|  | L | N | PVC | CPVC |
| 1/2” | 50.0 | 5.6 | 0.035 | 0.038 |
| 3/4” | 56.0 | 5.2 | 0.048 | 0.052 |
| 1” | 63.0 | 5.8 | 0.073 | 0.080 |
| 1-1/4” | 69.0 | 5.5 | 0.118 | 0.129 |
| 1-1/2” | 75.0 | 5.1 | 0.164 | 0.179 |
| 2” | 85.0 | 8.8 | 0.248 | 0.271 |
| 2-1/2” | 96.0 | 7.1 | 0.388 | 0.424 |
| 3” | 102.0 | 6.7 | 0.588 | 0.642 |
| 4” | 123.0 | 8.7 | 0.907 | 0.990 |

L

| Size | Inch | Weight (lb/pc) |
| --- | --- | --- |
|  | L | N | PVC | CPVC |
| 3/4" x 1/2" | 2.11 | 0.23 | 0.058 | 0.063 |
| 1" x 1/2" | 2.36 | 0.37 | 0.093 | 0.102 |
| 1" x 3/4" | 2.36 | 0.23 | 0.088 | 0.096 |
| 1-1/4" x 1/2" | 2.68 | 0.55 | 0.139 | 0.152 |
| 1-1/4" x 3/4" | 2.68 | 0.43 | 0.134 | 0.146 |
| 1-1/4" x 1" | 2.68 | 0.30 | 0.154 | 0.168 |
| 1-1/2" x 1/2" | 2.95 | 0.70 | 0.182 | 0.198 |
| 1-1/2" x 3/4" | 2.95 | 0.58 | 0.177 | 0.193 |
| 1-1/2" x 1" | 2.95 | 0.45 | 0.197 | 0.215 |
| 1-1/2" x 1-1/4" | 2.95 | 0.33 | 0.218 | 0.238 |
| 2" x 1/2" | 3.27 | 0.89 | 0.259 | 0.282 |
| 2" x 3/4" | 3.27 | 0.77 | 0.252 | 0.276 |
| 2" x 1" | 3.27 | 0.64 | 0.272 | 0.297 |
| 2" x 1-1/4" | 3.27 | 0.52 | 0.294 | 0.321 |
| 2" x 1-1/2" | 3.27 | 0.39 | 0.311 | 0.340 |
| 2-1/2" x 1-1/2" | 3.66 | 0.54 | 0.452 | 0.493 |
| 2-1/2" x 2" | 3.66 | 0.41 | 0.488 | 0.533 |
| 3" x 1" | 4.17 | 1.17 | 0.697 | 0.761 |
| 3" x 1-1/2" | 4.17 | 0.92 | 0.690 | 0.753 |
| 3" x 2" | 4.17 | 0.61 | 0.974 | 1.064 |
| 3" x 2-1/2" | 4.17 | 0.55 | 0.793 | 0.866 |
| 4" x 2" | 4.92 | 1.17 | 1.121 | 1.223 |
| 4" x 2-1/2" | 4.92 | 0.92 | 1.177 | 1.285 |
| 4" x 3" | 4.92 | 0.80 | 1.314 | 1.434 |
| 5" x 4" | 5.67 | 0.74 | 2.044 | 2.231 |
| 6" x 3" | 6.61 | 2.17 | 3.317 | 3.620 |
| 6" x 4" | 6.61 | 1.29 | 3.108 | 3.393 |
| 6" x 5" | 6.61 | 0.87 | 3.287 | 3.588 |
| 8" x 4" | 8.58 | 2.28 | 6.052 | 6.606 |
| 8" x 6" | 8.58 | 1.46 | 6.504 | 7.099 |
| 10" x 8" | 11.30 | 1.73 | 12.369 | 13.501 |
| 12" x 8" | 12.91 | 2.76 | 18.080 | 19.736 |
| 12" x 10" | 12.91 | 1.30 | 19.326 | 21.095 |

N

Ống và phụ kiện CPVC Sch80

| Size | mm | Weight (kg/pc) |
| --- | --- | --- |
|  | L | N | PVC | CPVC |
| 3/4" x 1/2" | 53.5 | 5.9 | 0.026 | 0.029 |
| 1" x 1/2" | 60.0 | 9.3 | 0.042 | 0.046 |
| 1" x 3/4" | 60.0 | 5.9 | 0.040 | 0.044 |
| 1-1/4" x 1/2" | 68.0 | 14.0 | 0.063 | 0.069 |
| 1-1/4" x 3/4" | 68.0 | 10.8 | 0.061 | 0.066 |
| 1-1/4" x 1" | 68.0 | 7.7 | 0.070 | 0.076 |
| 1-1/2" x 1/2" | 75.0 | 17.9 | 0.083 | 0.090 |
| 1-1/2" x 3/4" | 75.0 | 14.7 | 0.080 | 0.088 |
| 1-1/2" x 1" | 75.0 | 11.5 | 0.089 | 0.098 |
| 1-1/2" x 1-1/4" | 75.0 | 8.3 | 0.099 | 0.108 |
| 2" x 1/2" | 83.0 | 22.7 | 0.118 | 0.128 |
| 2" x 3/4" | 83.0 | 19.5 | 0.115 | 0.125 |
| 2" x 1" | 83.0 | 16.3 | 0.124 | 0.135 |
| 2" x 1-1/4" | 83.0 | 13.2 | 0.134 | 0.146 |
| 2" x 1-1/2" | 83.0 | 10.0 | 0.142 | 0.154 |
| 2-1/2" x 1-1/2" | 93.0 | 13.6 | 0.205 | 0.224 |
| 2-1/2" x 2" | 93.0 | 10.5 | 0.222 | 0.242 |
| 3" x 1" | 106.0 | 29.8 | 0.317 | 0.346 |
| 3" x 1-1/2" | 106.0 | 23.4 | 0.313 | 0.342 |
| 3" x 2" | 106.0 | 15.6 | 0.443 | 0.483 |
| 3" x 2-1/2" | 106.0 | 13.9 | 0.361 | 0.394 |
| 4" x 2" | 125.0 | 29.8 | 0.509 | 0.556 |
| 4" x 2-1/2" | 125.0 | 23.4 | 0.535 | 0.584 |
| 4" x 3" | 125.0 | 20.2 | 0.597 | 0.652 |
| 5" x 4" | 144.0 | 18.9 | 0.929 | 1.014 |
| 6" x 3" | 168.0 | 55.0 | 1.508 | 1.646 |
| 6" x 4" | 168.0 | 32.8 | 1.413 | 1.542 |
| 6" x 5" | 168.0 | 22.0 | 1.494 | 1.631 |
| 8" x 4" | 218.0 | 57.9 | 2.751 | 3.003 |
| 8" x 6" | 218.0 | 37.0 | 2.956 | 3.227 |
| 10" x 8" | 287.0 | 44.0 | 5.622 | 6.137 |
| 12" x 8" | 328.0 | 70.0 | 8.218 | 8.971 |
| 12" x 10" | 328.0 | 33.0 | 8.784 | 9.589 |

Inlet Size

| Size | Inch | Weight (lb/pc) |
| --- | --- | --- |
|  | G | H | PVC | CPVC |
| 1/2” | 0.602 | 1.476 | 0.08 | 0.09 |
| 3/4” | 0.673 | 1.673 | 0.10 | 0.11 |
| 1” | 0.843 | 1.969 | 0.18 | 0.19 |
| 1-1/4” | 1.033 | 2.283 | 0.31 | 0.34 |
| 1-1/2” | 1.184 | 2.559 | 0.41 | 0.44 |
| 2” | 1.413 | 2.913 | 0.59 | 0.65 |
| 2-1/2” | 1.754 | 3.504 | 1.02 | 1.11 |
| 3” | 2.101 | 3.976 | 1.70 | 1.85 |
| 4” | 2.514 | 4.764 | 2.73 | 2.98 |
| 5” | 3.130 | 5.807 | 4.81 | 5.25 |
| 6” | 3.740 | 6.811 | 7.77 | 8.48 |
| 8” | 4.803 | 8.858 | 15.70 | 17.13 |
| 10” | 5.906 | 11.417 | 23.43 | 25.58 |
| 12” | 6.890 | 12.992 | 39.95 | 43.61 |

| Size | mm | Weight (kg/pc) |
| --- | --- | --- |
|  | G | H | PVC | CPVC |
| 1/2” | 15 | 37.5 | 0.037 | 0.040 |
| 3/4” | 17 | 42.5 | 0.045 | 0.049 |
| 1” | 21 | 50.0 | 0.080 | 0.087 |
| 1-1/4” | 26 | 58.0 | 0.140 | 0.153 |
| 1-1/2” | 30 | 65.0 | 0.185 | 0.202 |
| 2” | 36 | 74.0 | 0.270 | 0.295 |
| 2-1/2” | 45 | 89.0 | 0.464 | 0.506 |
| 3” | 53 | 101.0 | 0.771 | 0.842 |
| 4” | 64 | 121.0 | 1.240 | 1.354 |
| 5” | 80 | 147.5 | 2.185 | 2.385 |
| 6” | 95 | 173.0 | 3.530 | 3.853 |
| 8” | 122 | 225.0 | 7.135 | 7.788 |
| 10” | 150 | 290.0 | 10.650 | 11.625 |
| 12” | 175 | 330.0 | 18.160 | 19.823 |

Eslon Sch80 PVC and CPVC Pipe and Fittings

| Size | Inch | Weight (lb/pc) |
| --- | --- | --- |
|  | G | H | PVC | CPVC |
| 1/2” | 0.602 | 1.476 | 0.11 | 1.19 |
| 3/4” | 0.673 | 1.673 | 0.15 | 1.64 |
| 1” | 0.843 | 1.969 | 0.27 | 2.91 |
| 1-1/4” | 1.033 | 2.283 | 0.44 | 4.78 |
| 1-1/2” | 1.184 | 2.559 | 0.63 | 6.84 |
| 2” | 1.413 | 2.913 | 0.94 | 10.27 |
| 2-1/2” | 1.754 | 3.504 | 1.58 | 17.20 |
| 3” | 2.101 | 3.976 | 2.88 | 31.43 |
| 4” | 2.514 | 4.764 | 4.76 | 51.98 |

| Size | mm | Weight (kg/pc) |
| --- | --- | --- |
|  | G | H | PVC | CPVC |
| 1/2” | 15 | 37.5 | 0.050 | 0.054 |
| 3/4” | 17 | 42.5 | 0.068 | 0.074 |
| 1” | 21 | 50.0 | 0.121 | 0.132 |
| 1-1/4” | 26 | 58.0 | 0.199 | 0.217 |
| 1-1/2” | 30 | 65.0 | 0.285 | 0.311 |
| 2” | 36 | 74.0 | 0.428 | 0.467 |
| 2-1/2” | 45 | 89.0 | 0.716 | 0.782 |
| 3” | 53 | 101.0 | 1.309 | 1.429 |
| 4” | 64 | 121.0 | 2.165 | 2.363 |

| Size | mm | Weight (kg/pc) |
| --- | --- | --- |
|  | G | H | PVC | CPVC |
| 1/2” | 15 | 37.5 | 0.041 | 0.045 |
| 3/4” | 17 | 42.5 | 0.051 | 0.056 |
| 1” | 21 | 50.0 | 0.090 | 0.098 |
| 1-1/4” | 26 | 58.0 | 0.155 | 0.169 |
| 1-1/2” | 30 | 65.0 | 0.205 | 0.224 |
| 2” | 36 | 74.0 | 0.299 | 0.327 |
| 2-1/2” | 45 | 89.0 | 0.516 | 0.563 |
| 3” | 53 | 101.0 | 0.842 | 0.919 |
| 4” | 64 | 121.0 | 1.365 | 1.490 |

| Size | Inch | Weight (lb/pc) |
| --- | --- | --- |
|  | G | H | PVC | CPVC |
| 1/2” | 0.602 | 1.476 | 0.09 | 0.10 |
| 3/4” | 0.673 | 1.673 | 0.11 | 0.12 |
| 1” | 0.843 | 1.969 | 0.20 | 0.22 |
| 1-1/4” | 1.033 | 2.283 | 0.34 | 0.37 |
| 1-1/2” | 1.184 | 2.559 | 0.45 | 0.49 |
| 2” | 1.413 | 2.913 | 0.66 | 0.72 |
| 2-1/2” | 1.754 | 3.504 | 1.14 | 1.24 |
| 3” | 2.101 | 3.976 | 1.85 | 2.02 |
| 4” | 2.514 | 4.764 | 3.00 | 3.28 |

H

H

Ống và phụ kiện CPVC Sch80

| Size | mm | Weight (kg/pc) |
| --- | --- | --- |
|  | J | H | PVC | CPVC |
| 1/2” | 7 | 29 | 0.030 | 0.033 |
| 3/4” | 9 | 34 | 0.040 | 0.044 |
| 1” | 8 | 37 | 0.064 | 0.070 |
| 1-1/4” | 11 | 43 | 0.102 | 0.111 |
| 1-1/2” | 12 | 47 | 0.130 | 0.142 |
| 2” | 17 | 55 | 0.190 | 0.207 |
| 2-1/2” | 20 | 64 | 0.359 | 0.392 |
| 3” | 24 | 72 | 0.580 | 0.633 |
| 4” | 29 | 86 | 0.915 | 0.999 |
| 5” | 38 | 106 | 1.595 | 1.741 |
| 6” | 46 | 124 | 2.580 | 2.816 |
| 8” | 55 | 158 | 4.925 | 5.376 |
| 10” | 70 | 210 | 7.446 | 8.317 |
| 12” | 85 | 240 | 15.330 | 16.733 |

Eslon Sch80 PVC and CPVC Pipe and Fittings

H

G

| Size | Inch | Weight (lb/pc) |
| --- | --- | --- |
|  | G | H | PVC | CPVC |
| 1/2” | 0.602 | 1.476 | 0.11 | 0.12 |
| 3/4” | 0.673 | 1.673 | 0.14 | 0.16 |
| 1” | 0.843 | 1.969 | 0.23 | 0.25 |
| 1-1/4” | 1.033 | 2.283 | 0.41 | 0.44 |
| 1-1/2” | 1.184 | 2.559 | 0.52 | 0.56 |
| 2” | 1.413 | 2.913 | 0.78 | 0.85 |
| 2-1/2” | 1.754 | 3.504 | 1.36 | 1.49 |
| 3” | 2.101 | 3.976 | 2.22 | 2.43 |
| 4” | 2.514 | 4.764 | 3.48 | 3.80 |
| 5” | 3.130 | 5.807 | 5.91 | 6.45 |
| 6” | 3.740 | 6.811 | 9.52 | 10.39 |
| 8” | 4.803 | 8.858 | 19.76 | 21.57 |
| 10” | 5.906 | 11.417 | 33.55 | 36.62 |
| 12” | 6.890 | 12.992 | 50.60 | 55.23 |

| Size | mm | Weight (kg/pc) |
| --- | --- | --- |
|  | G | H | PVC | CPVC |
| 1/2” | 15.3 | 37.5 | 0.050 | 0.055 |
| 3/4” | 17.1 | 42.5 | 0.065 | 0.071 |
| 1” | 21.4 | 50.0 | 0.105 | 0.115 |
| 1-1/4” | 26.3 | 58.0 | 0.184 | 0.201 |
| 1-1/2” | 30.1 | 65.0 | 0.235 | 0.257 |
| 2” | 35.9 | 74.0 | 0.355 | 0.388 |
| 2-1/2” | 44.6 | 89.0 | 0.619 | 0.676 |
| 3” | 53.4 | 101.0 | 1.010 | 1.102 |
| 4” | 63.9 | 121.0 | 1.581 | 1.726 |
| 5” | 79.5 | 147.5 | 2.684 | 2.930 |
| 6” | 95.0 | 173.0 | 4.325 | 4.721 |
| 8” | 122.0 | 225.0 | 8.980 | 9.802 |
| 10” | 150.0 | 290.0 | 15.250 | 16.646 |
| 12” | 175.0 | 330.0 | 23.000 | 25.106 |

H

G

| Size | Inch | Weight (lb/pc) |
| --- | --- | --- |
|  | G | H | PVC | CPVC |
| 1/2” | 0.602 | 1.476 | 0.15 | 0.16 |
| 3/4” | 0.673 | 1.673 | 0.20 | 0.22 |
| 1” | 0.843 | 1.969 | 0.33 | 0.36 |
| 1-1/4” | 1.033 | 2.283 | 0.55 | 0.60 |
| 1-1/2” | 1.184 | 2.559 | 0.74 | 0.80 |
| 2” | 1.413 | 2.913 | 1.11 | 1.21 |
| 2-1/2” | 1.754 | 3.504 | 1.91 | 2.08 |
| 3” | 2.101 | 3.976 | 3.23 | 3.52 |
| 4” | 2.514 | 4.764 | 5.14 | 5.61 |

| Size | mm | Weight (kg/pc) |
| --- | --- | --- |
|  | G | H | PVC | CPVC |
| 1/2” | 15.3 | 37.5 | 0.066 | 0.072 |
| 3/4” | 17.1 | 42.5 | 0.091 | 0.099 |
| 1” | 21.4 | 50.0 | 0.150 | 0.164 |
| 1-1/4” | 26.3 | 58.0 | 0.249 | 0.272 |
| 1-1/2” | 30.1 | 65.0 | 0.334 | 0.365 |
| 2” | 35.9 | 74.0 | 0.503 | 0.549 |
| 2-1/2” | 44.6 | 89.0 | 0.866 | 0.946 |
| 3” | 53.4 | 101.0 | 1.467 | 1.601 |
| 4” | 63.9 | 121.0 | 2.336 | 2.550 |

H

G

Eslon Sch80 PVC and CPVC Pipe and Fittings

| Size | Inch | Weight (lb/pc) |
| --- | --- | --- |
|  | G | H | PVC | CPVC |
| 1/2” | 0.602 | 1.476 | 0.12 | 0.13 |
| 3/4” | 0.673 | 1.673 | 0.16 | 0.17 |
| 1” | 0.843 | 1.969 | 0.25 | 0.28 |
| 1-1/4” | 1.033 | 2.283 | 0.44 | 0.48 |
| 1-1/2” | 1.184 | 2.559 | 0.56 | 0.61 |
| 2” | 1.413 | 2.913 | 0.85 | 0.92 |
| 2-1/2” | 1.754 | 3.504 | 1.48 | 1.61 |
| 3” | 2.101 | 3.976 | 2.38 | 2.60 |
| 4” | 2.514 | 4.764 | 3.75 | 4.10 |

| Size | mm | Weight (kg/pc) |
| --- | --- | --- |
|  | G | H | PVC | CPVC |
| 1/2” | 15.3 | 37.5 | 0.054 | 0.059 |
| 3/4” | 17.1 | 42.5 | 0.071 | 0.077 |
| 1” | 21.4 | 50.0 | 0.115 | 0.125 |
| 1-1/4” | 26.3 | 58.0 | 0.199 | 0.217 |
| 1-1/2” | 30.1 | 65.0 | 0.255 | 0.278 |
| 2” | 35.9 | 74.0 | 0.384 | 0.420 |
| 2-1/2” | 44.6 | 89.0 | 0.671 | 0.733 |
| 3” | 53.4 | 101.0 | 1.081 | 1.180 |
| 4” | 63.9 | 121.0 | 1.706 | 1.862 |

Eslon Sch80 PVC and CPVC Pipe and Fittings

H2

G2

G1

| Size | Inch | Weight (lb/pc) |
| --- | --- | --- |
|  | G1 | G2 | H1 | H2 | PVC | CPVC |
| 3/4" x 1/2" | 0.673 | 0.700 | 1.673 | 1.575 | 0.13 | 0.15 |
| 1" x 1/2" | 0.843 | 0.857 | 1.969 | 1.732 | 0.21 | 0.24 |
| 1" x 3/4" | 0.843 | 1.520 | 1.969 | 1.811 | 0.22 | 0.24 |
| 1-1/4" x 1/2" | 1.033 | 1.015 | 2.283 | 1.890 | 0.33 | 0.37 |
| 1-1/4" x 3/4" | 1.033 | 1.047 | 2.283 | 2.047 | 0.34 | 0.38 |
| 1-1/4" x 1" | 1.033 | 1.080 | 2.283 | 2.205 | 0.35 | 0.39 |
| 1-1/2" x 1/2" | 1.184 | 1.172 | 2.559 | 2.047 | 0.44 | 0.49 |
| 1-1/2" x 3/4" | 1.184 | 1.165 | 2.559 | 2.165 | 0.44 | 0.50 |
| 1-1/2" x 1" | 1.184 | 1.158 | 2.559 | 2.283 | 0.46 | 0.51 |
| 1-1/2" x 1-1/4" | 1.184 | 1.191 | 2.559 | 2.441 | 0.48 | 0.53 |
| 2" x 1/2" | 1.413 | 1.409 | 2.913 | 2.283 | 0.62 | 0.69 |
| 2" x 3/4" | 1.413 | 1.402 | 2.913 | 2.402 | 0.62 | 0.70 |
| 2" x 1" | 1.413 | 1.434 | 2.913 | 2.559 | 0.64 | 0.72 |
| 2" x 1-1/4" | 1.413 | 1.427 | 2.913 | 2.677 | 0.67 | 0.75 |
| 2" x 1-1/2" | 1.413 | 1.459 | 2.913 | 2.835 | 0.69 | 0.77 |
| 2-1/2" x 1-1/2" | 1.754 | 1.656 | 3.504 | 3.031 | 1.18 | 1.31 |
| 2-1/2" x 2" | 1.754 | 1.728 | 3.504 | 3.228 | 1.21 | 1.36 |
| 3" x 1-1/2" | 2.101 | 1.971 | 3.976 | 3.346 | 1.56 | 1.75 |
| 3" x 2" | 2.101 | 2.043 | 3.976 | 3.543 | 1.61 | 1.80 |
| 3" x 2-1/2" | 2.101 | 2.069 | 3.976 | 3.819 | 1.69 | 1.89 |
| 4" x 2" | 2.513 | 2.476 | 4.764 | 3.976 | 2.92 | 3.26 |
| 4" x 2-1/2" | 2.514 | 2.502 | 4.764 | 4.252 | 2.92 | 3.26 |
| 4" x 3" | 2.514 | 2.534 | 4.764 | 4.409 | 3.04 | 3.39 |
| 5" x 4" | 3.130 | 3.144 | 5.807 | 5.394 | 4.37 | 4.88 |
| 6" x 3" | 3.740 | 3.755 | 6.811 | 5.630 | 7.37 | 8.23 |
| 6" x 4" | 3.740 | 3.774 | 6.811 | 6.024 | 7.32 | 8.18 |
| 6" x 5" | 3.740 | 3.819 | 6.811 | 6.496 | 7.48 | 8.36 |
| 8" x 3" | 4.803 | 4.818 | 8.858 | 6.693 | 16.98 | 18.97 |
| 8" x 4" | 4.803 | 4.837 | 8.858 | 7.087 | 17.29 | 19.32 |
| 8" x 6" | 4.803 | 4.843 | 8.858 | 7.913 | 17.86 | 19.95 |
| 10" x 4" | 5.906 | 6.057 | 11.417 | 8.307 | 30.82 | 34.43 |
| 10" x 8" | 5.906 | 6.220 | 11.417 | 10.276 | 31.13 | 34.77 |
| 12" x 4" | 6.890 | 7.205 | 12.992 | 8.307 | 48.18 | 53.82 |
| 12" x 8" | 6.890 | 7.205 | 12.992 | 11.260 | 47.52 | 53.08 |
| 12" x 10" | 6.890 | 6.890 | 12.992 | 12.402 | 47.08 | 52.59 |

Main Size

Ống và phụ kiện CPVC Sch80

| Size | Inch | Weight (lb/pc) |
| --- | --- | --- |
|  | G1 | G2 | H1 | H2 | PVC | CPVC |
| 3/4" x 1/2" | 0.673 | 0.700 | 1.673 | 1.575 | 0.15 | 0.17 |
| 1" x 1/2" | 0.843 | 0.857 | 1.969 | 1.732 | 0.23 | 0.25 |
| 1" x 3/4" | 0.843 | 1.520 | 1.969 | 1.811 | 0.24 | 0.27 |
| 1-1/4" x 1/2" | 1.033 | 1.015 | 2.283 | 1.890 | 0.35 | 0.39 |
| 1-1/4" x 3/4" | 1.033 | 1.047 | 2.283 | 2.047 | 0.37 | 0.41 |
| 1-1/4" x 1" | 1.033 | 1.080 | 2.283 | 2.205 | 0.39 | 0.44 |
| 1-1/2" x 1/2" | 1.184 | 1.172 | 2.559 | 2.047 | 0.46 | 0.51 |
| 1-1/2" x 3/4" | 1.184 | 1.165 | 2.559 | 2.165 | 0.47 | 0.53 |
| 1-1/2" x 1" | 1.184 | 1.158 | 2.559 | 2.283 | 0.50 | 0.56 |
| 1-1/2" x 1-1/4" | 1.184 | 1.191 | 2.559 | 2.441 | 0.54 | 0.60 |
| 2" x 1/2" | 1.413 | 1.409 | 2.913 | 2.283 | 0.64 | 0.71 |
| 2" x 3/4" | 1.413 | 1.402 | 2.913 | 2.402 | 0.65 | 0.73 |
| 2" x 1" | 1.413 | 1.434 | 2.913 | 2.559 | 0.69 | 0.77 |
| 2" x 1-1/4" | 1.413 | 1.427 | 2.913 | 2.677 | 0.73 | 0.82 |
| 2" x 1-1/2" | 1.413 | 1.459 | 2.913 | 2.835 | 0.78 | 0.87 |
| 2-1/2" x 1-1/2" | 1.754 | 1.656 | 3.504 | 3.031 | 1.26 | 1.41 |
| 2-1/2" x 2" | 1.754 | 1.728 | 3.504 | 3.228 | 1.34 | 1.50 |
| 3" x 1-1/2" | 2.101 | 1.971 | 3.976 | 3.346 | 1.65 | 1.85 |
| 3" x 2" | 2.101 | 2.043 | 3.976 | 3.543 | 1.74 | 1.95 |
| 3" x 2-1/2" | 2.101 | 2.069 | 3.976 | 3.819 | 1.92 | 2.14 |
| 4" x 2" | 2.513 | 2.476 | 4.764 | 3.976 | 3.05 | 3.41 |
| 4" x 2-1/2" | 2.514 | 2.502 | 4.764 | 4.252 | 3.15 | 3.51 |
| 4" x 3" | 2.514 | 2.534 | 4.764 | 4.409 | 3.35 | 3.74 |
| 5" x 4" | 3.130 | 3.144 | 5.807 | 5.394 | 4.64 | 5.18 |
| 6" x 3" | 3.740 | 3.755 | 6.811 | 5.630 | 7.68 | 8.58 |
| 6" x 4" | 3.740 | 3.774 | 6.811 | 6.024 | 7.87 | 8.79 |
| 8" x 3" | 4.803 | 4.818 | 8.858 | 6.693 | 17.30 | 19.32 |
| 8" x 4" | 4.803 | 4.837 | 8.858 | 7.087 | 17.84 | 19.93 |
| 10" x 4" | 5.906 | 6.057 | 11.417 | 8.307 | 31.10 | 34.74 |
| 12" x 4" | 6.890 | 7.205 | 12.992 | 8.307 | 47.36 | 52.90 |

Ống và phụ kiện CPVC Sch80

H2

G2

G1

Ống và phụ kiện CPVC Sch80

| Size | Inch | Weight (lb/pc) |
| --- | --- | --- |
|  | L | L1 | S | PVC | CPVC |
| 3/4" x 1/2" | 1.260 | 0.906 | 1.181 | 0.03 | 0.03 |
| 1" x 1/2" | 1.378 | 0.906 | 1.496 | 0.06 | 0.07 |
| 1" x 3/4" | 1.378 | 1.024 | 1.496 | 0.04 | 0.05 |
| 1-1/4" x 1/2" | 1.575 | 0.906 | 1.811 | 0.11 | 0.13 |
| 1-1/4" x 3/4" | 1.575 | 1.024 | 1.811 | 0.11 | 0.12 |
| 1-1/4" x 1" | 1.575 | 1.142 | 1.811 | 0.08 | 0.09 |
| 1-1/2" x 1/2" | 1.693 | 0.906 | 2.087 | 0.15 | 0.16 |
| 1-1/2" x 3/4" | 1.693 | 1.024 | 2.087 | 0.15 | 0.17 |
| 1-1/2" x 1" | 1.693 | 1.142 | 2.087 | 0.13 | 0.14 |
| 1-1/2" x 1-1/4" | 1.693 | 1.260 | 2.087 | 0.07 | 0.08 |
| 2" x 1/2" | 1.969 | 0.906 | 2.598 | 0.25 | 0.28 |
| 2" x 3/4" | 1.969 | 1.024 | 2.598 | 0.25 | 0.28 |
| 2" x 1" | 1.969 | 1.142 | 2.598 | 0.26 | 0.29 |
| 2" x 1-1/4" | 1.969 | 1.260 | 2.598 | 0.23 | 0.25 |
| 2" x 1-1/2" | 1.969 | 1.378 | 2.598 | 0.19 | 0.21 |
| 2-1/2" x 1-1/2" | 2.165 | 1.378 | 3.071 | 0.35 | 0.39 |
| 2-1/2" x 2" | 2.165 | 1.535 | 3.071 | 0.26 | 0.29 |
| 3" x 1" | 2.283 | 1.142 | 3.701 | 0.54 | 0.60 |
| 3" x 1-1/2" | 2.283 | 1.378 | 3.701 | 0.57 | 0.63 |
| 3" x 2" | 2.283 | 1.535 | 3.701 | 0.54 | 0.60 |
| 3" x 2-1/2" | 2.283 | 1.772 | 3.701 | 0.38 | 0.43 |
| 4" x 1" | 2.756 | 1.142 | 4.724 | 1.19 | 1.33 |
| 4" x 1-1/4" | 2.756 | 1.260 | 4.724 | 1.32 | 1.48 |
| 4" x 1-1/2" | 2.756 | 1.378 | 4.724 | 1.31 | 1.47 |
| 4" x 2" | 2.756 | 1.535 | 4.724 | 1.01 | 1.13 |
| 4" x 2-1/2" | 2.756 | 1.772 | 4.724 | 0.92 | 1.03 |
| 4" x 3" | 2.756 | 1.890 | 4.724 | 0.78 | 0.87 |
| 5" x 4" | 3.228 | 2.283 | 5.906 | 1.04 | 1.16 |
| 6" x 3" | 3.622 | 1.890 | 6.890 | 2.47 | 2.76 |
| 6" x 4" | 3.622 | 2.283 | 6.890 | 2.75 | 3.07 |
| 6" x 5" | 3.622 | 2.677 | 6.890 | 1.88 | 2.10 |
| 8" x 4" | 4.724 | 2.283 | 9.055 | 4.80 | 5.36 |
| 8" x 6" | 4.724 | 3.031 | 9.055 | 5.41 | 6.04 |
| 10" x 6" | 6.299 | 3.031 | 11.220 | 9.21 | 10.28 |
| 10" x 8" | 6.299 | 4.016 | 11.220 | 10.23 | 11.42 |
| 12" x 6" | 6.850 | 3.071 | 13.386 | 16.00 | 17.87 |
| 12" x 8" | 6.850 | 4.055 | 13.386 | 16.69 | 18.64 |
| 12" x 10" | 6.850 | 5.512 | 13.386 | 14.57 | 16.28 |

Ống và phụ kiện CPVC Sch80

S

L1

| Size | mm | Weight (kg/pc) |
| --- | --- | --- |
|  | L | L1 | S | PVC | CPVC |
| 3/4" x 1/2" | 32 | 23 | 30 | 0.012 | 0.013 |
| 1" x 1/2" | 35 | 23 | 38 | 0.027 | 0.030 |
| 1" x 3/4" | 35 | 26 | 38 | 0.019 | 0.021 |
| 1-1/4" x 1/2" | 40 | 23 | 46 | 0.051 | 0.057 |
| 1-1/4" x 3/4" | 40 | 26 | 46 | 0.048 | 0.054 |
| 1-1/4" x 1" | 40 | 29 | 46 | 0.036 | 0.040 |
| 1-1/2" x 1/2" | 43 | 23 | 53 | 0.067 | 0.075 |
| 1-1/2" x 3/4" | 43 | 26 | 53 | 0.068 | 0.076 |
| 1-1/2" x 1" | 43 | 29 | 53 | 0.058 | 0.065 |
| 1-1/2" x 1-1/4" | 43 | 32 | 53 | 0.034 | 0.038 |
| 2" x 1/2" | 50 | 23 | 66 | 0.114 | 0.127 |
| 2" x 3/4" | 50 | 26 | 66 | 0.114 | 0.127 |
| 2" x 1" | 50 | 29 | 66 | 0.116 | 0.130 |
| 2" x 1-1/4" | 50 | 32 | 66 | 0.103 | 0.115 |
| 2" x 1-1/2" | 50 | 35 | 66 | 0.085 | 0.095 |
| 2-1/2" x 1-1/2" | 55 | 35 | 78 | 0.160 | 0.179 |
| 2-1/2" x 2" | 55 | 39 | 78 | 0.118 | 0.132 |
| 3" x 1" | 58 | 29 | 94 | 0.244 | 0.273 |
| 3" x 1-1/2" | 58 | 35 | 94 | 0.258 | 0.288 |
| 3" x 2" | 58 | 39 | 94 | 0.245 | 0.274 |
| 3" x 2-1/2" | 58 | 45 | 94 | 0.173 | 0.193 |
| 4" x 1" | 70 | 29 | 120 | 0.540 | 0.603 |
| 4" x 1-1/4" | 70 | 32 | 120 | 0.602 | 0.672 |
| 4" x 1-1/2" | 70 | 35 | 120 | 0.597 | 0.667 |
| 4" x 2" | 70 | 39 | 120 | 0.460 | 0.514 |
| 4" x 2-1/2" | 70 | 45 | 120 | 0.420 | 0.469 |
| 4" x 3" | 70 | 48 | 120 | 0.354 | 0.395 |
| 5" x 4" | 82 | 58 | 150 | 0.474 | 0.529 |
| 6" x 3" | 92 | 48 | 175 | 1.123 | 1.254 |
| 6" x 4" | 92 | 58 | 175 | 1.250 | 1.396 |
| 6" x 5" | 92 | 68 | 175 | 0.853 | 0.953 |
| 8" x 4" | 120 | 58 | 230 | 2.180 | 2.435 |
| 8" x 6" | 120 | 77 | 230 | 2.458 | 2.746 |
| 10" x 6" | 160 | 77 | 285 | 4.185 | 4.675 |
| 10" x 8" | 160 | 102 | 285 | 4.648 | 5.192 |
| 12" x 6" | 174 | 78 | 340 | 7.271 | 8.122 |
| 12" x 8" | 174 | 103 | 340 | 7.585 | 8.472 |
| 12" x 10" | 174 | 140 | 340 | 6.624 | 7.399 |

|  | Bushing |
| --- | --- |
|  | 1/2" | 3/4" | 1" | 1-1/4" | 1-1/2" | 2" | 2-1/2" | 3" | 4" | 5" | 6" | 8" | 10" | 12" |
| Bushing | 1/2" |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 3/4" | + |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 1" | + | + |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 1-1/4" | + | + | + |  |  |  |  |  |  |  |  |  |  |  |
|  | 1-1/2" | + | + | + | + |  |  |  |  |  |  |  |  |  |  |
|  | 2" | + | + | + | + | + |  |  |  |  |  |  |  |  |  |
|  | 2-1/2" | +B | +B | +B | +B | + | + |  |  |  |  |  |  |  |  |
|  | 3" | +B | +B | + | +B | + | + | + |  |  |  |  |  |  |  |
|  | 4" | +B | +B | + | + | + | + | + | + |  |  |  |  |  |  |
|  | 5" | +B*2 | +B*2 | +B | +B | +B | +B | +B | +B | + |  |  |  |  |  |
|  | 6" | +B*2 | +B*2 | +B | +B | +B | +B | +B | + | + | + |  |  |  |  |
|  | 8" | +B*2 | +B*2 | +B | +B | +B | +B | +B | +B | + | +B | + |  |  |  |
|  | 10" | - | - | +B*2 | +B*2 | +B*2 | +B*2 | +B*2 | +B*2 | +B | +B | + | + |  |  |
|  | 12" | - | - | +B*2 | +B*2 | +B*2 | +B*2 | +B*2 | +B*2 | +B | +B | + | + | + |  |

S

L1

| Size | Inch | Weight (lb/pc) |
| --- | --- | --- |
|  | L | L1 | S | PVC | CPVC |
| 3/4" x 1/2" | 1.260 | 0.906 | 1.181 | 0.03 | 0.03 |
| 1" x 1/2" | 1.378 | 0.906 | 1.496 | 0.06 | 0.07 |
| 1" x 3/4" | 1.378 | 1.024 | 1.496 | 0.05 | 0.06 |
| 1-1/4" x 1/2" | 1.575 | 0.906 | 1.811 | 0.12 | 0.13 |
| 1-1/4" x 3/4" | 1.575 | 1.024 | 1.811 | 0.10 | 0.12 |
| 1-1/4" x 1" | 1.575 | 1.142 | 1.811 | 0.10 | 0.11 |
| 1-1/2" x 1/2" | 1.693 | 0.906 | 2.087 | 0.18 | 0.20 |
| 1-1/2" x 3/4" | 1.693 | 1.024 | 2.087 | 0.20 | 0.23 |
| 1-1/2" x 1" | 1.693 | 1.142 | 2.087 | 0.13 | 0.15 |
| 1-1/2" x 1-1/4" | 1.693 | 1.260 | 2.087 | 0.09 | 0.10 |
| 2" x 1/2" | 1.969 | 0.906 | 2.598 | 0.26 | 0.29 |
| 2" x 3/4" | 1.969 | 1.024 | 2.598 | 0.27 | 0.31 |
| 2" x 1" | 1.969 | 1.142 | 2.598 | 0.28 | 0.32 |
| 2" x 1-1/4" | 1.969 | 1.260 | 2.598 | 0.23 | 0.26 |
| 2" x 1-1/2" | 1.969 | 1.378 | 2.598 | 0.19 | 0.22 |
| 2-1/2" x 1-1/2" | 2.165 | 1.378 | 3.071 | 0.45 | 0.51 |
| 2-1/2" x 2" | 2.165 | 1.535 | 3.071 | 0.28 | 0.32 |
| 3" x 1" | 2.283 | 1.142 | 3.701 | 0.68 | 0.76 |
| 3" x 1-1/2" | 2.283 | 1.378 | 3.701 | 0.67 | 0.75 |
| 3" x 2" | 2.283 | 1.535 | 3.701 | 0.68 | 0.77 |
| 3" x 2-1/2" | 2.283 | 1.772 | 3.701 | 0.45 | 0.51 |
| 4" x 1" | 2.756 | 1.142 | 4.724 | 0.02 | 0.02 |
| 4" x 1-1/4" | 2.756 | 1.260 | 4.724 | 0.03 | 0.04 |
| 4" x 1-1/2" | 2.756 | 1.378 | 4.724 | 1.44 | 1.61 |
| 4" x 2" | 2.756 | 1.535 | 4.724 | 1.11 | 1.25 |
| 4" x 2-1/2" | 2.756 | 1.772 | 4.724 | 0.98 | 1.10 |
| 4" x 3" | 2.756 | 1.890 | 4.724 | 0.88 | 0.98 |
| 5" x 4" | 3.228 | 2.283 | 5.906 | 1.48 | 1.65 |
| 6" x 4" | 3.622 | 2.283 | 6.890 | 2.31 | 2.58 |
| 8" x 4" | 4.724 | 2.283 | 9.055 | 8.60 | 9.60 |

| Size | mm | Weight (kg/pc) |
| --- | --- | --- |
|  | L | L1 | S | PVC | CPVC |
| 3/4" x 1/2" | 32 | 23 | 30 | 0.013 | 0.014 |
| 1" x 1/2" | 35 | 23 | 38 | 0.027 | 0.030 |
| 1" x 3/4" | 35 | 26 | 38 | 0.024 | 0.027 |
| 1-1/4" x 1/2" | 40 | 23 | 46 | 0.054 | 0.060 |
| 1-1/4" x 3/4" | 40 | 26 | 46 | 0.047 | 0.052 |
| 1-1/4" x 1" | 40 | 29 | 46 | 0.046 | 0.052 |
| 1-1/2" x 1/2" | 43 | 23 | 53 | 0.081 | 0.091 |
| 1-1/2" x 3/4" | 43 | 26 | 53 | 0.092 | 0.103 |
| 1-1/2" x 1" | 43 | 29 | 53 | 0.060 | 0.067 |
| 1-1/2" x 1-1/4" | 43 | 32 | 53 | 0.042 | 0.047 |
| 2" x 1/2" | 50 | 23 | 66 | 0.117 | 0.131 |
| 2" x 3/4" | 50 | 26 | 66 | 0.124 | 0.139 |
| 2" x 1" | 50 | 29 | 66 | 0.128 | 0.143 |
| 2" x 1-1/4" | 50 | 32 | 66 | 0.106 | 0.118 |
| 2" x 1-1/2" | 50 | 35 | 66 | 0.088 | 0.099 |
| 2-1/2" x 1-1/2" | 55 | 35 | 78 | 0.206 | 0.231 |
| 2-1/2" x 2" | 55 | 39 | 78 | 0.129 | 0.145 |
| 3" x 1" | 58 | 29 | 94 | 0.310 | 0.346 |
| 3" x 1-1/2" | 58 | 35 | 94 | 0.306 | 0.342 |
| 3" x 2" | 58 | 39 | 94 | 0.311 | 0.348 |
| 3" x 2-1/2" | 58 | 45 | 94 | 0.207 | 0.231 |
| 4" x 1" | 70 | 29 | 120 | 0.010 | 0.011 |
| 4" x 1-1/4" | 70 | 32 | 120 | 0.015 | 0.017 |
| 4" x 1-1/2" | 70 | 35 | 120 | 0.656 | 0.733 |
| 4" x 2" | 70 | 39 | 120 | 0.507 | 0.566 |
| 4" x 2-1/2" | 70 | 45 | 120 | 0.448 | 0.500 |
| 4" x 3" | 70 | 48 | 120 | 0.399 | 0.445 |
| 5" x 4" | 82 | 58 | 150 | 0.671 | 0.749 |
| 6" x 4" | 92 | 58 | 175 | 1.048 | 1.171 |
| 8" x 4" | 120 | 58 | 230 | 3.907 | 4.364 |

Ống và phụ kiện CPVC Sch80

Ống và phụ kiện CPVC Sch80

d

B

| Size | Inch | Weight (lb/pc) |
| --- | --- | --- |
|  | L | d | B | PVC | CPVC |
| 1/2” | 1.811 | 0.551 | 1.339 | 0.05 | 0.06 |
| 3/4” | 1.969 | 0.748 | 1.535 | 0.06 | 0.06 |
| 1” | 2.205 | 0.945 | 1.850 | 0.09 | 0.10 |
| 1-1/4” | 2.480 | 1.260 | 2.283 | 0.14 | 0.16 |
| 1-1/2” | 2.598 | 1.496 | 2.524 | 0.20 | 0.22 |
| 2” | 2.874 | 1.969 | 3.031 | 0.26 | 0.30 |
| 2-1/2” | 3.661 | 2.441 | 3.701 | 0.48 | 0.54 |
| 3” | 3.858 | 2.835 | 4.370 | 0.66 | 0.74 |
| 4” | 4.409 | 3.780 | 5.472 | 1.12 | 1.25 |

| Size | mm | Weight (kg/pc) |
| --- | --- | --- |
|  | L | d | B | PVC | CPVC |
| 1/2” | 46 | 14.0 | 34.0 | 0.023 | 0.026 |
| 3/4” | 50 | 19.0 | 39.0 | 0.025 | 0.028 |
| 1” | 56 | 24.0 | 47.0 | 0.040 | 0.045 |
| 1-1/4” | 63 | 32.0 | 58.0 | 0.064 | 0.071 |
| 1-1/2” | 66 | 38.0 | 64.1 | 0.090 | 0.101 |
| 2” | 73 | 50.0 | 77.0 | 0.120 | 0.134 |
| 2-1/2” | 93 | 62.0 | 94.0 | 0.220 | 0.246 |
| 3” | 98 | 72.0 | 111.0 | 0.300 | 0.335 |
| 4” | 112 | 96.0 | 139.0 | 0.510 | 0.570 |

| Size | Inch | Weight (lb/pc) |
| --- | --- | --- |
|  | L | G | PVC | CPVC |
| 1/2” | 0.220 | 1.969 | 0.07 | 0.07 |
| 3/4” | 0.205 | 2.205 | 0.09 | 0.10 |
| 1” | 0.230 | 2.480 | 0.14 | 0.15 |
| 1-1/4” | 0.217 | 2.717 | 0.23 | 0.25 |
| 1-1/2” | 0.202 | 2.953 | 0.32 | 0.34 |
| 2” | 0.346 | 3.346 | 0.48 | 0.53 |
| 2-1/2” | 0.280 | 3.780 | 0.74 | 0.81 |
| 3” | 0.265 | 4.016 | 1.14 | 1.24 |
| 4” | 0.343 | 4.843 | 1.72 | 1.88 |

| Size | mm | Weight (kg/pc) |
| --- | --- | --- |
|  | L | G | PVC | CPVC |
| 1/2” | 5.60 | 50.0 | 0.031 | 0.034 |
| 3/4” | 5.20 | 56.0 | 0.042 | 0.046 |
| 1” | 5.84 | 63.0 | 0.063 | 0.069 |
| 1-1/4” | 5.50 | 69.0 | 0.103 | 0.113 |
| 1-1/2” | 5.14 | 75.0 | 0.143 | 0.157 |
| 2” | 8.80 | 85.0 | 0.219 | 0.239 |
| 2-1/2” | 7.10 | 96.0 | 0.336 | 0.367 |
| 3” | 6.74 | 102.0 | 0.517 | 0.564 |
| 4” | 8.70 | 123.0 | 0.782 | 0.853 |

L

L

Ống và phụ kiện CPVC Sch80

| Size | mm | Weight (kg/pc) |
| --- | --- | --- |
|  | L | PVC | CPVC |
| 1/2” | 30.0 | 0.016 | 0.018 |
| 3/4” | 34.0 | 0.023 | 0.025 |
| 1” | 38.0 | 0.036 | 0.040 |
| 1-1/4” | 42.0 | 0.058 | 0.063 |
| 1-1/2” | 46.0 | 0.090 | 0.102 |
| 2” | 52.0 | 0.120 | 0.144 |
| 2-1/2” | 60.0 | 0.205 | 0.224 |
| 3” | 65.5 | 0.360 | 0.382 |
| 4” | 79.6 | 0.467 | 0.518 |
| 5” | 89.0 | 0.768 | 0.852 |
| 6” | 100.8 | 1.196 | 1.339 |
| 8” | 132 | 2.332 | 2.605 |
| 10” | 168 | 4.595 | 5.133 |
| 12” | 186 | 7.089 | 7.918 |

Ống và phụ kiện CPVC Sch80

| Size | Inch | Weight (lb/pc) |
| --- | --- | --- |
|  | L | PVC | CPVC |
| 1/2" | 0.96 | 0.03 | 0.033 |
| 3/4" | 0.98 | 0.04 | 0.044 |
| 1" | 1.10 | 0.06 | 0.065 |
| 1-1/4" | 1.28 | 0.11 | 0.120 |
| 1-1/2" | 1.30 | 0.13 | 0.142 |
| 2" | 1.44 | 0.20 | 0.218 |
| 2-1/2" | 1.97 | 0.30 | 0.327 |
| 3" | 2.05 | 0.44 | 0.480 |
| 4" | 2.15 | 0.75 | 0.819 |

| Size | mm | Weight (kg/pc) |
| --- | --- | --- |
|  | L | PVC | CPVC |
| 1/2” | 24.5 | 0.014 | 0.015 |
| 3/4” | 25.0 | 0.018 | 0.020 |
| 1” | 28.0 | 0.027 | 0.030 |
| 1-1/4” | 32.5 | 0.050 | 0.055 |
| 1-1/2” | 33.0 | 0.059 | 0.065 |
| 2” | 36.5 | 0.091 | 0.099 |
| 2-1/2” | 50.0 | 0.136 | 0.149 |
| 3” | 52.0 | 0.200 | 0.218 |
| 4” | 54.5 | 0.341 | 0.372 |

| Size | Inch | Weight (lb/pc) |
| --- | --- | --- |
|  | L | PVC | CPVC |
| 1/2” | (1-1/8"), 2", 3", 4", 5", 6", 8", 10", 12" | – | – |
| 3/4” | (1-3/8"), 2", 3", 4", 5", 6", 8", 10", 12" | – | – |
| 1” | (1-1/2"), 3", 4", 5", 6", 8", 10", 12" | – | – |
| 1-1/4” | (1-5/8"), 3", 4", 5", 6", 8", 10", 12" | – | – |
| 1-1/2” | (1-3/4"), 3", 4", 5", 6", 8", 10", 12" | – | – |
| 2” | (2"), 3", 4", 5", 6", 8", 10", 12" | – | – |
| 2-1/2” | (2-1/2"), 4", 5", 6", 8", 10", 12" | – | – |
| 3” | (2-5/8"), 4", 5", 6", 8", 10", 12" | – | – |
| 4” | (2-7/8"), 5", 6", 8", 10", 12" | – | – |

| Size | mm | Weight (kg/pc) |
| --- | --- | --- |
|  | L | PVC | CPVC |
| 1/2” | (1-1/8"), 2", 3", 4", 5", 6", 8", 10", 12" | – | – |
| 3/4” | (1-3/8"), 2", 3", 4", 5", 6", 8", 10", 12" | – | – |
| 1” | (1-1/2"), 3", 4", 5", 6", 8", 10", 12" | – | – |
| 1-1/4” | (1-5/8"), 3", 4", 5", 6", 8", 10", 12" | – | – |
| 1-1/2” | (1-3/4"), 3", 4", 5", 6", 8", 10", 12" | – | – |
| 2” | (2"), 3", 4", 5", 6", 8", 10", 12" | – | – |
| 2-1/2” | (2-1/2"), 4", 5", 6", 8", 10", 12" | – | – |
| 3” | (2-5/8"), 4", 5", 6", 8", 10", 12" | – | – |
| 4” | (2-7/8"), 5", 6", 8", 10", 12" | – | – |

| Size | Inch | Weight (lb/pc) |
| --- | --- | --- |
|  | L | G | PVC | CPVC |
| 1/2" | 2.047 | 0.315 | 0.11 | 0.12 |
| 3/4" | 2.323 | 0.354 | 0.17 | 0.19 |
| 1" | 2.638 | 0.354 | 0.31 | 0.34 |
| 1-1/4" | 2.992 | 0.472 | 0.48 | 0.53 |
| 1-1/2" | 3.228 | 0.472 | 0.64 | 0.69 |
| 2" | 3.622 | 0.630 | 1.00 | 1.09 |
| 2-1/2" | 4.252 | 0.709 | 1.56 | 1.70 |
| 3" | 4.724 | 0.945 | 2.52 | 2.76 |
| 4" | 5.984 | 1.417 | 4.37 | 4.77 |

G

| Size | Inch | Weight (lb/pc) |
| --- | --- | --- |
|  | L | G | PVC | CPVC |
| 1/2" | 2.047 | 0.315 | 0.10 | 0.11 |
| 3/4" | 2.323 | 0.354 | 0.16 | 0.18 |
| 1" | 2.638 | 0.354 | 0.29 | 0.31 |
| 1-1/4" | 2.992 | 0.472 | 0.45 | 0.49 |
| 1-1/2" | 3.228 | 0.472 | 0.59 | 0.65 |
| 2" | 3.622 | 0.630 | 0.94 | 1.02 |
| 2-1/2" | 4.252 | 0.709 | 1.44 | 1.58 |
| 3" | 4.724 | 0.945 | 2.37 | 2.58 |
| 4" | 5.984 | 1.417 | 4.10 | 4.47 |

Ống và phụ kiện CPVC Sch80

| Size | mm | Weight (kg/pc) |
| --- | --- | --- |
|  | L | G | PVC | CPVC |
| 1/2" | 52 | 8 | 0.050 | 0.054 |
| 3/4" | 59 | 9 | 0.079 | 0.086 |
| 1" | 67 | 9 | 0.140 | 0.153 |
| 1-1/4" | 76 | 12 | 0.219 | 0.239 |
| 1-1/2" | 82 | 12 | 0.289 | 0.316 |
| 2" | 92 | 16 | 0.455 | 0.497 |
| 2-1/2" | 108 | 18 | 0.708 | 0.773 |
| 3" | 120 | 24 | 1.147 | 1.252 |
| 4" | 152 | 36 | 1.987 | 2.169 |

| Size | Inch | Weight (lb/pc) |
| --- | --- | --- |
|  | L | t | PCD | D | n | h | PVC | CPVC |
| 1/2" | 0.992 | 0.461 | 2.382 | 3.504 | 4 | 0.630 | 0.21 | 0.23 |
| 3/4" | 1.161 | 0.516 | 2.756 | 3.858 | 4 | 0.630 | 0.26 | 0.30 |
| 1" | 1.260 | 0.598 | 3.130 | 4.252 | 4 | 0.630 | 0.42 | 0.47 |
| 1-1/4" | 1.512 | 0.665 | 3.504 | 4.606 | 4 | 0.630 | 0.53 | 0.59 |
| 1-1/2" | 1.594 | 0.720 | 3.878 | 5.000 | 4 | 0.630 | 0.68 | 0.76 |
| 2" | 1.772 | 0.748 | 4.744 | 5.984 | 4 | 0.748 | 1.01 | 1.13 |
| 2-1/2" | 1.988 | 0.984 | 5.492 | 7.008 | 4 | 0.748 | 1.57 | 1.76 |
| 3" | 1.988 | 1.004 | 6.004 | 7.520 | 4 | 0.748 | 1.94 | 2.16 |
| 4" | 2.492 | 1.118 | 7.500 | 9.016 | 8 | 0.748 | 2.95 | 3.29 |
| 5" | 2.992 | 1.122 | 8.504 | 10.000 | 8 | 0.866 | 3.63 | 4.05 |
| 6" | 3.327 | 1.024 | 9.508 | 10.984 | 8 | 0.866 | 4.88 | 5.46 |
| 8" | 4.567 | 1.142 | 11.752 | 13.504 | 8 | 0.866 | 7.48 | 8.36 |

Ống và phụ kiện CPVC Sch80

t

PCD

D

| Size | Inch | Weight (lb/pc) |
| --- | --- | --- |
|  | L | t | PCD | D | n | h | PVC | CPVC |
| 1/2" | 0.992 | 0.551 | 2.756 | 3.740 | 4 | 0.591 | 0.21 | 0.24 |
| 3/4" | 1.161 | 0.551 | 2.953 | 3.937 | 4 | 0.591 | 0.27 | 0.30 |
| 1" | 1.260 | 0.551 | 3.543 | 4.921 | 4 | 0.748 | 0.43 | 0.48 |
| 1-1/4" | 1.512 | 0.630 | 3.937 | 5.315 | 4 | 0.748 | 0.54 | 0.61 |
| 1-1/2" | 1.594 | 0.630 | 4.134 | 5.512 | 4 | 0.748 | 0.70 | 0.79 |
| 2" | 1.772 | 0.787 | 4.724 | 6.102 | 4 | 0.748 | 1.04 | 1.16 |
| 2-1/2" | 1.988 | 0.866 | 5.512 | 6.890 | 4 | 0.748 | 1.63 | 1.82 |
| 3" | 1.988 | 0.866 | 5.906 | 7.283 | 8 | 0.748 | 2.01 | 2.25 |
| 4" | 2.492 | 0.866 | 6.890 | 8.268 | 8 | 0.748 | 3.09 | 3.45 |
| 5" | 2.992 | 0.945 | 8.268 | 9.843 | 8 | 0.906 | 3.81 | 4.25 |
| 6" | 3.327 | 1.024 | 9.449 | 11.024 | 8 | 0.906 | 5.13 | 5.73 |
| 8" | 4.567 | 1.102 | 11.417 | 12.992 | 12 | 0.906 | 7.85 | 8.77 |

Ống và phụ kiện CPVC Sch80

t

PCD

D

| Size | Inch | Weight (lb/pc) |
| --- | --- | --- |
|  | L | t | PCD | D | n | h | PVC | CPVC |
| 1/2" | 0.992 | 0.461 | 2.382 | 3.504 | 4 | 0.630 | 0.22 | 0.24 |
| 3/4" | 1.161 | 0.516 | 2.756 | 3.858 | 4 | 0.630 | 0.28 | 0.31 |
| 1" | 1.260 | 0.598 | 3.130 | 4.252 | 4 | 0.630 | 0.44 | 0.49 |
| 1-1/4" | 1.512 | 0.665 | 3.504 | 4.606 | 4 | 0.630 | 0.56 | 0.63 |
| 1-1/2" | 1.594 | 0.720 | 3.878 | 5.000 | 4 | 0.630 | 0.73 | 0.81 |
| 2" | 1.772 | 0.748 | 4.744 | 5.984 | 4 | 0.748 | 1.07 | 1.20 |
| 2-1/2" | 1.988 | 0.984 | 5.492 | 7.008 | 4 | 0.748 | 1.69 | 1.89 |
| 3" | 1.988 | 1.004 | 6.004 | 7.520 | 4 | 0.748 | 2.09 | 2.34 |
| 4" | 2.492 | 1.118 | 7.500 | 9.016 | 8 | 0.748 | 3.22 | 3.60 |

Ống và phụ kiện CPVC Sch80

PCD

D

t

| Size | Inch | Weight (lb/pc) |
| --- | --- | --- |
|  | L | t | PCD | D | n | h | PVC | CPVC |
| 2" | 1.693 | 0.827 | 4.744 | 5.984 | 4 | 0.748 | 0.86 | 0.95 |
| 2-1/2" | 2.008 | 0.984 | 5.492 | 7.008 | 4 | 0.748 | 1.31 | 1.53 |
| 3" | 2.154 | 1.063 | 6.004 | 7.520 | 4 | 0.748 | 1.62 | 1.78 |
| 4" | 2.524 | 1.142 | 7.500 | 9.016 | 8 | 0.748 | 2.35 | 2.59 |
| 5" | 2.992 | 1.142 | 8.504 | 10.000 | 8 | 0.866 | 3.13 | 3.50 |
| 6" | 3.362 | 1.260 | 9.508 | 10.984 | 8 | 0.866 | 4.00 | 4.39 |
| 8" | 4.669 | 1.252 | 11.752 | 13.504 | 8 | 0.866 | 6.31 | 7.08 |
| 10" | 5.906 | 1.661 | 14.252 | 15.984 | 12 | 0.984 | 10.83 | 11.99 |
| 12" | 7.480 | 1.661 | 17.008 | 19.016 | 12 | 0.984 | 19.36 | 20.90 |

Ống và phụ kiện CPVC Sch80

PCD

D

t

Ống và phụ kiện CPVC Sch80

| Size | Inch | Weight (lb/pc) |
| --- | --- | --- |
|  | L | t | PCD | D | n | h | PVC | CPVC |
| 2" | 1.693 | 0.787 | 4.724 | 6.102 | 4 | 0.748 | 0.89 | 1.00 |
| 2-1/2" | 2.008 | 0.866 | 5.512 | 6.890 | 4 | 0.748 | 1.37 | 1.53 |
| 3" | 2.154 | 0.866 | 5.906 | 7.283 | 8 | 0.748 | 1.69 | 1.89 |
| 4" | 2.524 | 0.866 | 6.890 | 8.268 | 8 | 0.748 | 2.48 | 2.77 |
| 5" | 2.992 | 0.945 | 8.268 | 9.843 | 8 | 0.906 | 3.31 | 3.70 |
| 6" | 3.362 | 1.024 | 9.449 | 11.024 | 8 | 0.906 | 4.25 | 4.75 |
| 8" | 4.669 | 1.102 | 11.417 | 12.992 | 12 | 0.906 | 6.69 | 7.47 |
| 10" | 5.906 | 1.181 | 13.976 | 15.748 | 12 | 0.984 | 11.37 | 12.70 |
| 12" | 7.480 | 1.260 | 15.748 | 17.520 | 16 | 0.984 | 20.33 | 22.71 |

t

PCD

D

t

Ống và phụ kiện CPVC Sch80

PCD

D

| Size | Inch | Weight (lb/pc) |
| --- | --- | --- |
|  | t | PCD | D | n | h | PVC | CPVC |
| 1/2" | 0.571 | 2.382 | 3.504 | 4 | 0.630 | 0.24 | 0.27 |
| 3/4" | 0.630 | 2.756 | 3.858 | 4 | 0.630 | 0.33 | 0.36 |
| 1" | 0.748 | 3.130 | 4.252 | 4 | 0.630 | 0.47 | 0.53 |
| 1-1/4" | 0.748 | 3.504 | 4.606 | 4 | 0.630 | 0.56 | 0.62 |
| 1-1/2" | 0.748 | 3.878 | 5.000 | 4 | 0.630 | 0.65 | 0.72 |
| 2" | 0.827 | 4.744 | 5.984 | 4 | 0.748 | 1.02 | 1.14 |
| 2-1/2" | 0.984 | 5.492 | 7.008 | 4 | 0.748 | 1.66 | 1.86 |
| 3" | 1.063 | 6.004 | 7.520 | 4 | 0.748 | 2.04 | 2.28 |
| 4" | 1.260 | 7.500 | 9.016 | 8 | 0.748 | 3.30 | 3.69 |
| 5" | 1.260 | 8.504 | 10.000 | 8 | 0.866 | 3.84 | 4.29 |
| 6" | 1.378 | 9.508 | 10.984 | 8 | 0.866 | 4.90 | 5.48 |
| 8" | 1.437 | 11.752 | 13.504 | 8 | 0.866 | 7.50 | 8.38 |
| 10" | 1.693 | 14.252 | 15.984 | 12 | 0.984 | 16.60 | 18.54 |
| 12" | 1.693 | 17.008 | 19.016 | 12 | 0.984 | 23.82 | 26.61 |

NOTES:

Flange bolt

hole patt

erns meet

JIS B2220

| Size | Inch | Weight (lb/pc) | ft-lbs |
| --- | --- | --- | --- |
|  | d | D1 | D2 | PCD | D | n-φh |  |  |
| 1/2" | 0.709 | 1.181 | – | 2.362 | 3.386 | 4-5/8” | 0.06 | 12 |
| 3/4" | 0.866 | 1.181 | 1.654 | 2.756 | 3.780 | 4-5/8” | 0.07 | 12 |
| 1" | 1.142 | 1.457 | 1.969 | 3.110 | 4.134 | 4-5/8” | 0.10 | 12 |
| 1-1/4" | 1.496 | 1.811 | 2.323 | 3.504 | 4.528 | 4-5/8” | 0.11 | 26 |
| 1-1/2" | 1.693 | 2.087 | 2.677 | 3.858 | 4.921 | 4-5/8” | 0.13 | 26 |
| 2" | 2.126 | 2.520 | 3.268 | 4.764 | 5.906 | 4-3/4” | 0.14 | 26 |
| 2-1/2" | 2.717 | 3.189 | 3.976 | 5.512 | 6.890 | 4-3/4” | 0.18 | 38 |
| 3" | 3.150 | 3.622 | 4.409 | 5.984 | 7.402 | 4-3/4” | 0.19 | 38 |
| 4" | 4.055 | 4.882 | 5.827 | 7.480 | 8.898 | 8-3/4” | 0.23 | 38 |
| 5" | 5.079 | 5.906 | 6.850 | 8.504 | 9.921 | 8-7/8” | 0.29 | 46 |
| 6" | 6.024 | 6.772 | 7.717 | 9.488 | 10.906 | 8-7/8” | 0.35 | 46 |
| 8" | 7.874 | 8.740 | 9.685 | 11.732 | 13.386 | 8-7/8” | 0.44 | 46 |
| 10" | 10.000 | 10.866 | 11.811 | 14.252 | 15.906 | 12-1" | 0.64 | 55 |
| 12" | 12.008 | 13.189 | 14.370 | 17.008 | 18.898 | 12-1" | 0.75 | 55 |

Ống và phụ kiện CPVC Sch80

5

3

3.4

D1

D2

3

5

Eslon Sch80 PVC and CPVC Pipe and Fittings

| Size | Inch | Weight (lb/pc) | ft-lbs |
| --- | --- | --- | --- |
|  | d | D1 | D2 | PCD | D | n-φh |  |  |
| 1/2" | 0.709 | 1.181 | – | 2.362 | 3.386 | 4-5/8” | 0.05 | 11 |
| 3/4" | 0.866 | 1.181 | 1.654 | 2.756 | 3.780 | 4-5/8” | 0.06 | 11 |
| 1" | 1.142 | 1.457 | 1.969 | 3.110 | 4.134 | 4-5/8” | 0.09 | 22 |
| 1-1/4" | 1.496 | 1.811 | 2.323 | 3.504 | 4.528 | 4-5/8” | 0.10 | 22 |
| 1-1/2" | 1.693 | 2.087 | 2.677 | 3.858 | 4.921 | 4-5/8” | 0.11 | 22 |
| 2" | 2.126 | 2.520 | 3.268 | 4.764 | 5.906 | 4-3/4” | 0.12 | 22 |
| 2-1/2" | 2.717 | 3.189 | 3.976 | 5.512 | 6.890 | 4-3/4” | 0.17 | 33 |
| 3" | 3.150 | 3.622 | 4.409 | 5.984 | 7.402 | 4-3/4” | 0.17 | 33 |
| 4" | 4.055 | 4.882 | 5.827 | 7.480 | 8.898 | 8-3/4” | 0.21 | 33 |
| 5" | 5.079 | 5.906 | 6.850 | 8.504 | 9.921 | 8-7/8” | 0.25 | 40 |
| 6" | 6.024 | 6.772 | 7.717 | 9.488 | 10.906 | 8-7/8” | 0.32 | 40 |
| 8" | 7.874 | 8.740 | 9.685 | 11.732 | 13.386 | 8-7/8” | 0.41 | 40 |
| 10" | 10.000 | 10.866 | 11.811 | 14.252 | 15.906 | 12-1" | 0.55 | 48 |
| 12" | 12.008 | 13.189 | 14.370 | 17.008 | 18.898 | 12-1" | 0.61 | 48 |

3

| Normal Pipe Size (IPS) | Max. Operating Pressure at 73˚F (23˚C) |
| --- | --- |
|  | psi | MPa |
| 1/2 | 850 | 5.86 |
| 3/4 | 690 | 4.76 |
| 1 | 630 | 4.34 |
| 1 1/4 | 520 | 3.59 |
| 1 1/2 | 470 | 3.24 |
| 2 | 400 | 2.76 |
| 2 1/2 | 420 | 2.90 |
| 3 | 370 | 2.55 |
| 4 | 320 | 2.21 |
| 5 | 290 | 2.00 |
| 6 | 280 | 1.93 |
| 8 | 250 | 1.72 |
| 10 | 230 | 1.59 |
| 12 | 230 | 1.59 |
| 14 | 220 | 1.52 |
| 16 | 220 | 1.52 |
| 18 | 220 | 1.52 |
| 20 | 220 | 1.52 |
| 24 | 210 | 1.45 |

Engineering Data

Temperature degree Factor

Engineering Data

|  |  |  |  |  | PV | C |  | C | PV | C |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

|  |  |  | PV | C |  | CPV | C |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Temperature degree Factor

Engineering Data

Design Pressure (psi)

| 50 | 100 150 | 200 | 0 | 20 | 40 60 | 80 | 100 |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Temperature (°F) |  |  |  | Temperature (°C) |  |  |

Design Pressure (MPa)

Design Pressure (psi)

Design Pressure (MPa)

4"

1"

3/

4"

2"

2"

2-1/

3"

4"

5"

2"

2

6"

8"

4"

Hoop Stress (psi)

Hoop Stress (MPa)

d R

Engineering Data

sti

sti

Hoop Stress (psi)

40

Hoop Stress (MPa)

sti

sti

|  |  |  |  |  |  |  |  | CP | VC |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | P | VC |  |  |  |  |  |  |  |  |  |

Engineering Data

Tensile Strength (psi)

V

|  |  |  |  |  | C | PVC |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | P | C |  |  |  |  |  |

Tensile Strength (MPa)

Burst Pressure (psi)

3/

1"

4"

4"

2"

2"

Burst Pressure (MPa)

2

6"

8"

4"

4"

5"

6"

8"

24"

3/4"

1"

1-1/4"

1-1/2"

2"

2-1/2"

3"

1-1/

1-1/

2-1/

2"

3"

4"

5"

Engineering Data

Burst Pressure (psi)

Burst Pressure (MPa)

Engineering Data

0(

- F)

14

60(

°C)

Burst Hoop Stress (psi)

Burst Hoop Stress (MPa)

Burst Hoop Stress (psi)

7

3(

- F)

18

19

5(

4(

- F)

- F)

Burst Hoop Stress (MPa)

|  | 2 | 3( | C) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 6 | 0( | C) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 8 8 9 | 0( 5( 0( | C) C) C) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

PVC

C

PVC

Engineering Data

Loaded Stress (psi)

PVC

Loaded Stress (MPa)

CPVC

Engineering Data

Hydraulic Gradient (    )

Engineering Data

Hydraulic Gradient (    )

| Flow Rate | Flow Velocity V | Friction Head loss | Friction loss | FlowVe- locity V | Friction Head loss | Friction loss | Flow Velocity V | Friction Head loss | Friction loss | Flow Velocity V | Friction Head loss | Friction loss | Flow Rate |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Gallon/min | Liter/min | feet/sec | feet/100ft | psi/100ft | feet/sec | feet/100ft | psi/100ft | feet/sec | feet/100ft | psi/100ft | feet/sec | feet/100ft | psi/100ft | Gallon/min | Liter/min |
|  |  | 1/2” |  |  |  |  |  |  |  |  |  |  |  |
| 1 | 3.8 | 1.48 | 2.24 | 0.97 | 3/4” |  |  |  |  |  |  | 1 | 3.8 |
| 2 | 7.6 | 2.95 | 8.08 | 3.50 | 1.57 | 1.73 | 0.75 | 1” |  |  |  | 2 | 7.6 |
| 5 | 18.9 | 7.39 | 44.12 | 19.13 | 3.92 | 9.45 | 4.10 | 2.33 | 2.67 | 1.16 | 1-1/4” | 5 | 18.9 |
| 7 | 26.5 | 10.34 | 82.27 | 35.66 | 5.49 | 17.62 | 7.64 | 3.27 | 4.98 | 2.16 | 1.82 | 1.20 | 0.52 | 7 | 26.5 |
| 10 | 37.9 | 14.77 | 159.26 | 69.04 | 7.84 | 34.11 | 14.79 | 4.67 | 9.65 | 4.18 | 2.59 | 2.32 | 1.01 | 10 | 37.9 |
| 15 | 56.8 |  |  |  | 11.76 | 72.27 | 31.33 | 7.00 | 20.44 | 8.86 | 3.89 | 4.91 | 2.13 | 15 | 56.8 |
| 20 | 75.7 |  |  |  |  |  |  | 9.33 | 34.82 | 15.09 | 5.19 | 8.36 | 3.62 | 20 | 75.7 |
| 25 | 94.6 | 4” |  |  |  | 11.66 | 52.64 | 22.82 | 6.49 | 12.64 | 5.48 | 25 | 94.6 |
| 30 | 114 | 0.86 | 0.08 | 0.03 |  |  |  | 14.00 | 73.78 | 31.98 | 7.78 | 17.71 | 7.68 | 30 | 114 |
| 35 | 132 | 1.00 | 0.11 | 0.05 |  |  |  | 16.33 | 98.16 | 42.55 | 9.08 | 23.56 | 10.21 | 35 | 132 |
| 40 | 151 | 1.14 | 0.14 | 0.06 |  |  |  | 18.66 | 125.70 | 54.49 | 10.38 | 30.17 | 13.08 | 40 | 151 |
| 45 | 170 | 1.28 | 0.17 | 0.07 | 5” |  |  |  | 11.68 | 37.53 | 16.27 | 45 | 170 |
| 50 | 189 | 1.43 | 0.21 | 0.09 | 0.90 | 0.07 | 0.03 |  |  |  | 12.97 | 45.61 | 19.77 | 50 | 189 |
| 60 | 227 | 1.71 | 0.30 | 0.13 | 1.08 | 0.10 | 0.04 |  |  |  | 15.57 | 63.93 | 27.71 | 60 | 227 |
| 70 | 265 | 2.00 | 0.39 | 0.17 | 1.26 | 0.13 | 0.06 |  |  |  |  |  |  | 70 | 265 |
| 75 | 284 | 2.14 | 0.45 | 0.20 | 1.35 | 0.15 | 0.07 | 6” |  |  |  | 75 | 284 |
| 80 | 303 | 2.28 | 0.51 | 0.22 | 1.44 | 0.16 | 0.07 | 1.00 | 0.07 | 0.03 |  |  |  | 80 | 303 |
| 90 | 341 | 2.57 | 0.63 | 0.27 | 1.62 | 0.20 | 0.09 | 1.13 | 0.09 | 0.04 |  |  |  | 90 | 341 |
| 100 | 379 | 2.85 | 0.76 | 0.33 | 1.80 | 0.25 | 0.11 | 1.25 | 0.10 | 0.04 |  |  |  | 100 | 379 |
| 125 | 473 | 3.56 | 1.16 | 0.50 | 2.25 | 0.38 | 0.16 | 1.57 | 0.16 | 0.07 | 8” | 125 | 473 |
| 150 | 568 | 4.28 | 1.62 | 0.70 | 2.70 | 0.53 | 0.23 | 1.88 | 0.22 | 0.10 | 1.07 | 0.06 | 0.03 | 150 | 568 |
| 175 | 662 | 4.99 | 2.16 | 0.94 | 3.15 | 0.70 | 0.30 | 2.19 | 0.29 | 0.13 | 1.25 | 0.07 | 0.03 | 175 | 662 |
| 200 | 757 | 5.70 | 2.76 | 1.20 | 3.60 | 0.90 | 0.39 | 2.51 | 0.37 | 0.16 | 1.43 | 0.10 | 0.04 | 200 | 757 |
| 250 | 946 | 7.13 | 4.17 | 1.81 | 4.49 | 1.36 | 0.59 | 3.13 | 0.57 | 0.25 | 1.79 | 0.14 | 0.06 | 250 | 946 |
| 300 | 1136 | 8.55 | 5.85 | 2.54 | 5.39 | 1.90 | 0.82 | 3.76 | 0.79 | 0.34 | 2.14 | 0.20 | 0.09 | 300 | 1136 |
| 350 | 1325 | 9.98 | 7.78 | 3.37 | 6.29 | 2.53 | 1.10 | 4.39 | 1.05 | 0.46 | 2.50 | 0.27 | 0.12 | 350 | 1325 |
| 400 | 1514 | 11.41 | 9.96 | 4.32 | 7.19 | 3.24 | 1.40 | 5.02 | 1.35 | 0.59 | 2.86 | 0.34 | 0.15 | 400 | 1514 |
| 450 | 1703 |  |  |  | 8.09 | 4.04 | 1.75 | 5.64 | 1.68 | 0.73 | 3.21 | 0.43 | 0.19 | 450 | 1703 |
| 500 | 1893 |  |  |  | 8.99 | 4.90 | 2.12 | 6.27 | 2.04 | 0.88 | 3.57 | 0.52 | 0.23 | 500 | 1893 |
| 750 | 2839 | 18” |  |  |  | 9.40 | 4.33 | 1.88 | 5.36 | 1.10 | 0.48 | 750 | 2839 |
| 1000 | 3785 | 1.59 | 0.05 | 0.02 | 20” | 12.54 | 7.37 | 3.19 | 7.14 | 1.87 | 0.81 | 1000 | 3785 |
| 1250 | 4731 | 1.99 | 0.07 | 0.03 | 1.61 | 0.04 | 0.02 |  |  |  | 8.93 | 2.83 | 1.23 | 1250 | 4731 |
| 1500 | 5678 | 2.39 | 0.10 | 0.04 | 1.93 | 0.06 | 0.03 | 24” | 10.71 | 3.97 | 1.72 | 1500 | 5678 |
| 2000 | 7570 | 3.19 | 0.18 | 0.08 | 2.58 | 0.10 | 0.04 | 1.78 | 0.04 | 0.02 |  |  |  | 2000 | 7570 |
| 2500 | 9463 | 3.98 | 0.27 | 0.12 | 3.22 | 0.16 | 0.07 | 2.23 | 0.06 | 0.03 |  |  |  | 2500 | 9463 |
| 3000 | 11355 | 4.78 | 0.37 | 0.16 | 3.86 | 0.22 | 0.10 | 2.67 | 0.09 | 0.04 |  |  |  | 3000 | 11355 |
| 3500 | 13248 | 5.58 | 0.50 | 0.22 | 4.51 | 0.30 | 0.13 | 3.12 | 0.12 | 0.05 |  |  |  | 3500 | 13248 |
| 4000 | 15140 | 6.37 | 0.64 | 0.28 | 5.15 | 0.38 | 0.16 | 3.56 | 0.15 | 0.07 |  |  |  | 4000 | 15140 |
| 4500 | 17033 | 7.17 | 0.79 | 0.34 | 5.80 | 0.47 | 0.20 | 4.01 | 0.19 | 0.08 |  |  |  | 4500 | 17033 |
| 5000 | 18925 | 7.97 | 0.96 | 0.42 | 6.44 | 0.57 | 0.25 | 4.45 | 0.23 | 0.10 |  |  |  | 5000 | 18925 |
| 5500 | 20818 | 8.77 | 1.15 | 0.50 | 7.08 | 0.68 | 0.29 | 4.90 | 0.28 | 0.12 |  |  |  | 5500 | 20818 |
| 6000 | 22710 | 9.56 | 1.35 | 0.59 | 7.73 | 0.80 | 0.35 | 5.35 | 0.33 | 0.14 |  |  |  | 6000 | 22710 |
| 6500 | 24603 | 10.36 | 1.56 | 0.68 | 8.37 | 0.93 | 0.40 | 5.79 | 0.38 | 0.16 |  |  |  | 6500 | 24603 |
| 7000 | 26495 | 11.16 | 1.79 | 0.78 | 9.02 | 1.07 | 0.46 | 6.24 | 0.44 | 0.19 |  |  |  | 7000 | 26495 |
| 7500 | 28388 |  |  |  | 9.66 | 1.21 | 0.52 | 6.68 | 0.49 | 0.21 |  |  |  | 7500 | 28388 |
| 8000 | 30280 |  |  |  | 10.30 | 1.37 | 0.59 | 7.13 | 0.56 | 0.24 |  |  |  | 8000 | 30280 |
| 8500 | 32173 |  |  |  |  |  |  | 7.57 | 0.62 | 0.27 |  |  |  | 8500 | 32173 |
| 9000 | 34065 |  |  |  |  |  |  | 8.02 | 0.69 | 0.30 |  |  |  | 9000 | 34065 |
| 9500 | 35958 |  |  |  |  |  |  | 8.46 | 0.77 | 0.33 |  |  |  | 9500 | 35958 |
| 10000 | 37850 |  |  |  |  |  |  | 8.91 | 0.84 | 0.36 |  |  |  | 10000 | 37850 |

Engineering Data

Engineering Data

| Flow Rate | Flow Velocity V | Friction Head loss | Friction loss | Flow Velocity V | Friction Head loss | Friction loss | Flow Velocity V | Friction Head loss | Friction loss | Flow Velocity V | Friction Head loss | Friction loss | Flow Rate |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Gallon/min | Liter/min | feet/sec | feet/100ft | psi/100ft | feet/sec | feet/100ft | psi/100ft | feet/sec | feet/100ft | psi/100ft | feet/sec | feet/100ft | psi/100ft | Gallon/min | Liter/min |
| 1 | 3.8 |  |  |  |  |  |  |  |  |  |  |  |  | 1 | 3.8 |
| 2 | 7.6 |  |  |  |  |  |  |  |  |  |  |  |  | 2 | 7.6 |
| 5 | 18.9 |  |  |  |  |  |  |  |  |  |  |  |  | 5 | 18.9 |
| 7 | 26.5 | 1-1/2” |  |  |  |  |  |  |  |  |  | 7 | 26.5 |
| 10 | 37.9 | 1.88 | 1.05 | 0.46 | 2” |  |  |  |  |  |  | 10 | 37.9 |
| 15 | 56.8 | 2.81 | 2.23 | 0.97 | 1.68 | 0.63 | 0.27 | 2-1/2” |  |  |  | 15 | 56.8 |
| 20 | 75.7 | 3.75 | 3.80 | 1.65 | 2.23 | 1.07 | 0.46 | 1.56 | 0.45 | 0.20 | 3” | 20 | 75.7 |
| 25 | 94.6 | 4.69 | 5.74 | 2.49 | 2.79 | 1.63 | 0.71 | 1.95 | 0.68 | 0.29 | 1.25 | 0.23 | 0.10 | 25 | 94.6 |
| 30 | 114 | 5.63 | 8.04 | 3.49 | 3.35 | 2.28 | 0.99 | 2.34 | 0.95 | 0.41 | 1.49 | 0.32 | 0.14 | 30 | 114 |
| 35 | 132 | 6.57 | 10.70 | 4.64 | 3.91 | 3.03 | 1.31 | 2.73 | 1.26 | 0.55 | 1.74 | 0.43 | 0.19 | 35 | 132 |
| 40 | 151 | 7.50 | 13.70 | 5.94 | 4.47 | 3.88 | 1.68 | 3.12 | 1.62 | 0.70 | 1.99 | 0.54 | 0.23 | 40 | 151 |
| 45 | 170 | 8.44 | 17.05 | 7.39 | 5.03 | 4.83 | 2.09 | 3.51 | 2.01 | 0.87 | 2.24 | 0.68 | 0.29 | 45 | 170 |
| 50 | 189 | 9.38 | 20.72 | 8.98 | 5.58 | 5.87 | 2.54 | 3.90 | 2.44 | 1.06 | 2.49 | 0.82 | 0.36 | 50 | 189 |
| 60 | 227 | 11.26 | 29.04 | 12.59 | 6.70 | 8.22 | 3.56 | 4.68 | 3.43 | 1.49 | 2.99 | 1.15 | 0.50 | 60 | 227 |
| 70 | 265 |  |  |  | 7.82 | 10.94 | 4.74 | 5.46 | 4.56 | 1.98 | 3.49 | 1.54 | 0.67 | 70 | 265 |
| 75 | 284 |  |  |  | 8.38 | 12.43 | 5.39 | 5.85 | 5.18 | 2.25 | 3.74 | 1.74 | 0.75 | 75 | 284 |
| 80 | 303 |  |  |  | 8.93 | 14.01 | 6.07 | 6.23 | 5.84 | 2.53 | 3.99 | 1.97 | 0.85 | 80 | 303 |
| 90 | 341 |  |  |  | 10.05 | 17.42 | 7.55 | 7.01 | 7.26 | 3.15 | 4.48 | 2.45 | 1.06 | 90 | 341 |
| 100 | 379 |  |  |  | 11.17 | 21.18 | 9.18 | 7.79 | 8.83 | 3.83 | 4.98 | 2.97 | 1.29 | 100 | 379 |
| 125 | 473 |  |  |  | 13.96 | 32.01 | 13.88 | 9.74 | 13.34 | 5.78 | 6.23 | 4.49 | 1.95 | 125 | 473 |
| 150 | 568 |  |  |  |  |  |  | 11.69 | 18.70 | 8.11 | 7.47 | 6.30 | 2.73 | 150 | 568 |
| 175 | 662 |  |  |  |  |  |  | 13.64 | 24.88 | 10.79 | 8.72 | 8.38 | 3.63 | 175 | 662 |
| 200 | 757 |  |  |  |  |  |  |  |  |  | 9.97 | 10.73 | 4.65 | 200 | 757 |
| 250 | 946 | 10” |  |  |  |  |  |  | 12.46 | 16.22 | 7.03 | 250 | 946 |
| 300 | 1136 | 1.36 | 0.07 | 0.03 |  |  |  |  |  |  |  |  |  | 300 | 1136 |
| 350 | 1325 | 1.59 | 0.09 | 0.04 | 12” |  |  |  |  |  |  | 350 | 1325 |
| 400 | 1514 | 1.81 | 0.11 | 0.05 | 1.28 | 0.05 | 0.02 |  |  |  |  |  |  | 400 | 1514 |
| 450 | 1703 | 2.04 | 0.14 | 0.06 | 1.44 | 0.06 | 0.03 | 14” |  |  |  | 450 | 1703 |
| 500 | 1893 | 2.27 | 0.17 | 0.07 | 1.60 | 0.07 | 0.03 | 1.33 | 0.05 | 0.02 | 16” | 500 | 1893 |
| 750 | 2839 | 3.40 | 0.36 | 0.16 | 2.40 | 0.16 | 0.07 | 1.99 | 0.10 | 0.04 | 1.52 | 0.05 | 0.02 | 750 | 2839 |
| 1000 | 3785 | 4.54 | 0.62 | 0.27 | 3.20 | 0.27 | 0.12 | 2.65 | 0.17 | 0.07 | 2.02 | 0.09 | 0.04 | 1000 | 3785 |
| 1250 | 4731 | 5.67 | 0.94 | 0.41 | 4.01 | 0.40 | 0.17 | 3.32 | 0.25 | 0.11 | 2.53 | 0.13 | 0.06 | 1250 | 4731 |
| 1500 | 5678 | 6.80 | 1.32 | 0.57 | 4.81 | 0.56 | 0.24 | 3.98 | 0.36 | 0.16 | 3.03 | 0.18 | 0.08 | 1500 | 5678 |
| 2000 | 7570 | 9.07 | 2.24 | 0.97 | 6.41 | 0.96 | 0.42 | 5.31 | 0.61 | 0.26 | 4.05 | 0.31 | 0.13 | 2000 | 7570 |
| 2500 | 9463 | 11.34 | 3.39 | 1.47 | 8.01 | 1.46 | 0.63 | 6.63 | 0.92 | 0.40 | 5.06 | 0.48 | 0.21 | 2500 | 9463 |
| 3000 | 11355 |  |  |  | 9.61 | 2.04 | 0.88 | 7.96 | 1.29 | 0.56 | 6.07 | 0.67 | 0.29 | 3000 | 11355 |
| 3500 | 13248 |  |  |  | 11.21 | 2.71 | 1.17 | 9.29 | 1.72 | 0.75 | 7.08 | 0.89 | 0.39 | 3500 | 13248 |
| 4000 | 15140 |  |  |  |  |  |  | 10.62 | 2.20 | 0.95 | 8.09 | 1.14 | 0.49 | 4000 | 15140 |
| 4500 | 17033 |  |  |  |  |  |  |  |  |  | 9.10 | 1.41 | 0.61 | 4500 | 17033 |
| 5000 | 18925 |  |  |  |  |  |  |  |  |  | 10.12 | 1.72 | 0.75 | 5000 | 18925 |
| 5500 | 20818 |  |  |  |  |  |  |  |  |  |  |  |  | 5500 | 20818 |
| 6000 | 22710 |  |  |  |  |  |  |  |  |  |  |  |  | 6000 | 22710 |

| Flow Rate | Flow Velocity V | Friction Head loss | Friction loss | Flow Velocity V | Friction Head loss | Friction loss | Flow Velocity V | Friction Head loss | Friction loss | Flow Velocity V | Friction Head loss | Friction loss | Flow Rate |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Gallon/min | Liter/min | m/sec | m/100m | MPa/100m | m/sec | m/100m | MPa/100m | m/sec | m/100m | MPa/100m | m/sec | m/100m | MPa/100m | Gallon/min | Liter/min |
|  |  | 1/2" |  |  |  |  |  |  |  |  |  |  |  |
| 1 | 3.8 | 0.45 | 2.23 | 0.02 | 3/4" |  |  |  |  |  |  | 1 | 3.8 |
| 2 | 7.6 | 0.90 | 8.05 | 0.08 | 0.48 | 1.73 | 0.02 | 1" |  |  |  | 2 | 7.6 |
| 5 | 18.9 | 2.25 | 43.96 | 0.43 | 1.19 | 9.44 | 0.09 | 0.71 | 2.67 | 0.03 | 1-1/4" | 5 | 18.9 |
| 7 | 26.5 | 3.15 | 81.97 | 0.80 | 1.67 | 17.61 | 0.17 | 1.00 | 4.99 | 0.05 | 0.55 | 1.20 | 0.01 | 7 | 26.5 |
| 10 | 37.9 | 4.50 | 158.68 | 1.56 | 2.39 | 34.09 | 0.33 | 1.42 | 9.65 | 0.09 | 0.79 | 2.31 | 0.02 | 10 | 37.9 |
| 15 | 56.8 |  |  |  | 3.58 | 72.24 | 0.71 | 2.13 | 20.45 | 0.20 | 1.19 | 4.90 | 0.05 | 15 | 56.8 |
| 20 | 75.7 |  |  |  |  |  |  | 2.84 | 34.85 | 0.34 | 1.58 | 8.35 | 0.08 | 20 | 75.7 |
| 25 | 94.6 | 4" |  |  |  | 3.56 | 52.68 | 0.52 | 1.98 | 12.63 | 0.12 | 25 | 94.6 |
| 30 | 114 | 0.26 | 0.08 | 0.00 |  |  |  | 4.27 | 73.84 | 0.72 | 2.37 | 17.70 | 0.17 | 30 | 114 |
| 35 | 132 | 0.30 | 0.11 | 0.00 |  |  |  | 4.98 | 98.23 | 0.96 | 2.77 | 23.55 | 0.23 | 35 | 132 |
| 40 | 151 | 0.35 | 0.14 | 0.00 |  |  |  | 5.69 | 125.79 | 1.23 | 3.16 | 30.15 | 0.30 | 40 | 151 |
| 45 | 170 | 0.39 | 0.17 | 0.00 | 5" |  |  |  | 3.56 | 37.51 | 0.37 | 45 | 170 |
| 50 | 189 | 0.43 | 0.21 | 0.00 | 0.27 | 0.07 | 0.00 |  |  |  | 3.95 | 45.59 | 0.45 | 50 | 189 |
| 60 | 227 | 0.52 | 0.30 | 0.00 | 0.33 | 0.10 | 0.00 |  |  |  | 4.74 | 63.90 | 0.63 | 60 | 227 |
| 70 | 265 | 0.61 | 0.39 | 0.00 | 0.38 | 0.13 | 0.00 |  |  |  |  |  |  | 70 | 265 |
| 75 | 284 | 0.65 | 0.45 | 0.00 | 0.41 | 0.15 | 0.00 | 6" |  |  |  | 75 | 284 |
| 80 | 303 | 0.70 | 0.51 | 0.00 | 0.44 | 0.16 | 0.00 | 0.31 | 0.07 | 0.00 |  |  |  | 80 | 303 |
| 90 | 341 | 0.78 | 0.63 | 0.01 | 0.49 | 0.20 | 0.00 | 0.34 | 0.09 | 0.00 |  |  |  | 90 | 341 |
| 100 | 379 | 0.87 | 0.76 | 0.01 | 0.55 | 0.25 | 0.00 | 0.38 | 0.10 | 0.00 |  |  |  | 100 | 379 |
| 125 | 473 | 1.09 | 1.16 | 0.01 | 0.68 | 0.38 | 0.00 | 0.48 | 0.16 | 0.00 | 8" | 125 | 473 |
| 150 | 568 | 1.30 | 1.62 | 0.02 | 0.82 | 0.53 | 0.01 | 0.57 | 0.22 | 0.00 | 0.33 | 0.06 | 0.00 | 150 | 568 |
| 175 | 662 | 1.52 | 2.16 | 0.02 | 0.96 | 0.70 | 0.01 | 0.67 | 0.29 | 0.00 | 0.38 | 0.07 | 0.00 | 175 | 662 |
| 200 | 757 | 1.74 | 2.76 | 0.03 | 1.10 | 0.90 | 0.01 | 0.76 | 0.37 | 0.00 | 0.44 | 0.10 | 0.00 | 200 | 757 |
| 250 | 946 | 2.17 | 4.17 | 0.04 | 1.37 | 1.36 | 0.01 | 0.96 | 0.57 | 0.01 | 0.54 | 0.14 | 0.00 | 250 | 946 |
| 300 | 1136 | 2.61 | 5.85 | 0.06 | 1.64 | 1.90 | 0.02 | 1.15 | 0.79 | 0.01 | 0.65 | 0.20 | 0.00 | 300 | 1136 |
| 350 | 1325 | 3.04 | 7.78 | 0.08 | 1.92 | 2.53 | 0.02 | 1.34 | 1.05 | 0.01 | 0.76 | 0.27 | 0.00 | 350 | 1325 |
| 400 | 1514 | 3.48 | 9.96 | 0.10 | 2.19 | 3.24 | 0.03 | 1.53 | 1.35 | 0.01 | 0.87 | 0.34 | 0.00 | 400 | 1514 |
| 450 | 1703 |  |  |  | 2.47 | 4.04 | 0.04 | 1.72 | 1.68 | 0.02 | 0.98 | 0.43 | 0.00 | 450 | 1703 |
| 500 | 1893 |  |  |  | 2.74 | 4.91 | 0.05 | 1.91 | 2.04 | 0.02 | 1.09 | 0.52 | 0.01 | 500 | 1893 |
| 750 | 2839 | 18" |  |  |  | 2.87 | 4.32 | 0.04 | 1.63 | 1.10 | 0.01 | 750 | 2839 |
| 1000 | 3785 | 0.49 | 0.05 | 0.00 | 20" | 3.82 | 7.37 | 0.07 | 2.18 | 1.87 | 0.02 | 1000 | 3785 |
| 1250 | 4731 | 0.61 | 0.07 | 0.00 | 0.49 | 0.04 | 0.00 |  |  |  | 2.72 | 2.83 | 0.03 | 1250 | 4731 |
| 1500 | 5678 | 0.73 | 0.10 | 0.00 | 0.59 | 0.06 | 0.00 | 24" | 3.26 | 3.97 | 0.04 | 1500 | 5678 |
| 2000 | 7570 | 0.97 | 0.18 | 0.00 | 0.79 | 0.10 | 0.00 | 0.54 | 0.04 | 0.00 |  |  |  | 2000 | 7570 |
| 2500 | 9463 | 1.21 | 0.27 | 0.00 | 0.98 | 0.16 | 0.00 | 0.68 | 0.06 | 0.00 |  |  |  | 2500 | 9463 |
| 3000 | 11355 | 1.46 | 0.37 | 0.00 | 1.18 | 0.22 | 0.00 | 0.81 | 0.09 | 0.00 |  |  |  | 3000 | 11355 |
| 3500 | 13248 | 1.70 | 0.50 | 0.00 | 1.37 | 0.30 | 0.00 | 0.95 | 0.12 | 0.00 |  |  |  | 3500 | 13248 |
| 4000 | 15140 | 1.94 | 0.64 | 0.01 | 1.57 | 0.38 | 0.00 | 1.09 | 0.15 | 0.00 |  |  |  | 4000 | 15140 |
| 4500 | 17033 | 2.19 | 0.79 | 0.01 | 1.77 | 0.47 | 0.00 | 1.22 | 0.19 | 0.00 |  |  |  | 4500 | 17033 |
| 5000 | 18925 | 2.43 | 0.96 | 0.01 | 1.96 | 0.57 | 0.01 | 1.36 | 0.23 | 0.00 |  |  |  | 5000 | 18925 |
| 5500 | 20818 | 2.67 | 1.15 | 0.01 | 2.16 | 0.68 | 0.01 | 1.49 | 0.28 | 0.00 |  |  |  | 5500 | 20818 |
| 6000 | 22710 | 2.91 | 1.35 | 0.01 | 2.36 | 0.80 | 0.01 | 1.63 | 0.33 | 0.00 |  |  |  | 6000 | 22710 |
| 6500 | 24603 | 3.16 | 1.56 | 0.02 | 2.55 | 0.93 | 0.01 | 1.77 | 0.38 | 0.00 |  |  |  | 6500 | 24603 |
| 7000 | 26495 | 3.40 | 1.79 | 0.02 | 2.75 | 1.07 | 0.01 | 1.90 | 0.44 | 0.00 |  |  |  | 7000 | 26495 |
| 7500 | 28388 |  |  |  | 2.94 | 1.21 | 0.01 | 2.04 | 0.49 | 0.00 |  |  |  | 7500 | 28388 |
| 8000 | 30280 |  |  |  | 3.14 | 1.37 | 0.01 | 2.17 | 0.56 | 0.01 |  |  |  | 8000 | 30280 |
| 8500 | 32173 |  |  |  |  |  |  | 2.31 | 0.62 | 0.01 |  |  |  | 8500 | 32173 |
| 9000 | 34065 |  |  |  |  |  |  | 2.44 | 0.69 | 0.01 |  |  |  | 9000 | 34065 |
| 9500 | 35958 |  |  |  |  |  |  | 2.58 | 0.77 | 0.01 |  |  |  | 9500 | 35958 |
| 10000 | 37850 |  |  |  |  |  |  | 2.72 | 0.84 | 0.01 |  |  |  | 10000 | 37850 |

Engineering Data

Engineering Data

| Flow Rate | Flow Velocity V | Friction Head loss | Friction loss | Flow Velocity V | Friction Head loss | Friction loss | Flow Velocity V | Friction Head loss | Friction loss | Flow Velocity V | Friction Head loss | Friction loss | Flow Rate |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Gallon/min | Liter/min | m/sec | m/100m | MPa/100m | m/sec | m/100m | MPa/100m | m/sec | m/100m | MPa/100m | m/sec | m/100m | MPa/100m | Gallon/min | Liter/min |
| 1 | 3.8 |  |  |  |  |  |  |  |  |  |  |  |  | 1 | 3.8 |
| 2 | 7.6 |  |  |  |  |  |  |  |  |  |  |  |  | 2 | 7.6 |
| 5 | 18.9 |  |  |  |  |  |  |  |  |  |  |  |  | 5 | 18.9 |
| 7 | 26.5 | 1-1/2" |  |  |  |  |  |  |  |  |  | 7 | 26.5 |
| 10 | 37.9 | 0.57 | 1.05 | 0.01 | 2" |  |  |  |  |  |  | 10 | 37.9 |
| 15 | 56.8 | 0.86 | 2.23 | 0.02 | 0.51 | 0.63 | 0.01 | 2-1/2" |  |  |  | 15 | 56.8 |
| 20 | 75.7 | 1.14 | 3.80 | 0.04 | 0.68 | 1.07 | 0.01 | 0.47 | 0.45 | 0.00 | 3" | 20 | 75.7 |
| 25 | 94.6 | 1.43 | 5.74 | 0.06 | 0.85 | 1.62 | 0.02 | 0.59 | 0.68 | 0.01 | 0.38 | 0.23 | 0.00 | 25 | 94.6 |
| 30 | 114 | 1.72 | 8.04 | 0.08 | 1.02 | 2.28 | 0.02 | 0.71 | 0.95 | 0.01 | 0.46 | 0.32 | 0.00 | 30 | 114 |
| 35 | 132 | 2.00 | 10.70 | 0.10 | 1.19 | 3.03 | 0.03 | 0.83 | 1.26 | 0.01 | 0.53 | 0.43 | 0.00 | 35 | 132 |
| 40 | 151 | 2.29 | 13.70 | 0.13 | 1.36 | 3.88 | 0.04 | 0.95 | 1.62 | 0.02 | 0.61 | 0.54 | 0.01 | 40 | 151 |
| 45 | 170 | 2.57 | 17.04 | 0.17 | 1.53 | 4.83 | 0.05 | 1.07 | 2.01 | 0.02 | 0.68 | 0.68 | 0.01 | 45 | 170 |
| 50 | 189 | 2.86 | 20.72 | 0.20 | 1.70 | 5.87 | 0.06 | 1.19 | 2.44 | 0.02 | 0.76 | 0.82 | 0.01 | 50 | 189 |
| 60 | 227 | 3.43 | 29.04 | 0.28 | 2.04 | 8.22 | 0.08 | 1.42 | 3.43 | 0.03 | 0.91 | 1.15 | 0.01 | 60 | 227 |
| 70 | 265 | 4.00 | 38.63 | 0.38 | 2.38 | 10.94 | 0.11 | 1.66 | 4.56 | 0.04 | 1.06 | 1.53 | 0.02 | 70 | 265 |
| 75 | 284 |  |  |  | 2.55 | 12.43 | 0.12 | 1.78 | 5.18 | 0.05 | 1.14 | 1.74 | 0.02 | 75 | 284 |
| 80 | 303 |  |  |  | 2.72 | 14.01 | 0.14 | 1.90 | 5.84 | 0.06 | 1.21 | 1.97 | 0.02 | 80 | 303 |
| 90 | 341 |  |  |  | 3.06 | 17.42 | 0.17 | 2.14 | 7.26 | 0.07 | 1.37 | 2.44 | 0.02 | 90 | 341 |
| 100 | 379 |  |  |  | 3.40 | 21.17 | 0.21 | 2.37 | 8.82 | 0.09 | 1.52 | 2.97 | 0.03 | 100 | 379 |
| 125 | 473 |  |  |  | 4.25 | 32.01 | 0.31 | 2.97 | 13.34 | 0.13 | 1.90 | 4.49 | 0.04 | 125 | 473 |
| 150 | 568 |  |  |  |  |  |  | 3.56 | 18.69 | 0.18 | 2.28 | 6.30 | 0.06 | 150 | 568 |
| 175 | 662 |  |  |  |  |  |  | 4.16 | 24.87 | 0.24 | 2.66 | 8.38 | 0.08 | 175 | 662 |
| 200 | 757 |  |  |  |  |  |  |  |  |  | 3.04 | 10.73 | 0.11 | 200 | 757 |
| 250 | 946 | 10" |  |  |  |  |  |  | 3.80 | 16.22 | 0.16 | 250 | 946 |
| 300 | 1136 | 0.41 | 0.06 | 0.00 |  |  |  |  |  |  |  |  |  | 300 | 1136 |
| 350 | 1325 | 0.48 | 0.09 | 0.00 | 12" |  |  |  |  |  |  | 350 | 1325 |
| 400 | 1514 | 0.55 | 0.11 | 0.00 | 0.39 | 0.05 | 0.00 |  |  |  |  |  |  | 400 | 1514 |
| 450 | 1703 | 0.62 | 0.14 | 0.00 | 0.44 | 0.06 | 0.00 | 14" |  |  |  | 450 | 1703 |
| 500 | 1893 | 0.69 | 0.17 | 0.00 | 0.49 | 0.07 | 0.00 | 0.40 | 0.05 | 0.00 | 16" | 500 | 1893 |
| 750 | 2839 | 1.04 | 0.36 | 0.00 | 0.73 | 0.16 | 0.00 | 0.61 | 0.10 | 0.00 | 0.46 | 0.05 | 0.00 | 750 | 2839 |
| 1000 | 3785 | 1.38 | 0.62 | 0.01 | 0.98 | 0.27 | 0.00 | 0.81 | 0.17 | 0.00 | 0.62 | 0.09 | 0.00 | 1000 | 3785 |
| 1250 | 4731 | 1.73 | 0.94 | 0.01 | 1.22 | 0.40 | 0.00 | 1.01 | 0.25 | 0.00 | 0.77 | 0.13 | 0.00 | 1250 | 4731 |
| 1500 | 5678 | 2.07 | 1.32 | 0.01 | 1.46 | 0.56 | 0.01 | 1.21 | 0.36 | 0.00 | 0.92 | 0.18 | 0.00 | 1500 | 5678 |
| 2000 | 7570 | 2.76 | 2.24 | 0.02 | 1.95 | 0.96 | 0.01 | 1.62 | 0.61 | 0.01 | 1.23 | 0.31 | 0.00 | 2000 | 7570 |
| 2500 | 9463 | 3.46 | 3.39 | 0.03 | 2.44 | 1.45 | 0.01 | 2.02 | 0.92 | 0.01 | 1.54 | 0.48 | 0.00 | 2500 | 9463 |
| 3000 | 11355 |  |  |  | 2.93 | 2.04 | 0.02 | 2.43 | 1.29 | 0.01 | 1.85 | 0.67 | 0.01 | 3000 | 11355 |
| 3500 | 13248 |  |  |  | 3.42 | 2.71 | 0.03 | 2.83 | 1.72 | 0.02 | 2.16 | 0.89 | 0.01 | 3500 | 13248 |
| 4000 | 15140 |  |  |  |  |  |  | 3.24 | 2.20 | 0.02 | 2.47 | 1.14 | 0.01 | 4000 | 15140 |
| 4500 | 17033 |  |  |  |  |  |  | 3.64 | 2.73 | 0.03 | 2.77 | 1.41 | 0.01 | 4500 | 17033 |
| 5000 | 18925 |  |  |  |  |  |  |  |  |  | 3.08 | 1.72 | 0.02 | 5000 | 18925 |
| 5500 | 20818 |  |  |  |  |  |  |  |  |  |  |  |  | 5500 | 20818 |
| 6000 | 22710 |  |  |  |  |  |  |  |  |  |  |  |  | 6000 | 22710 |

Engineering Data

| Nominal Pipe Size (inch) | Tee Run | Tee Branch | 90° Elbow | 45° Elbow |
| --- | --- | --- | --- | --- |
|  | f=0.35 | f=1.2 | f=1 | f=0.4 |
| 1/2” | 0.65 | 2.23 | 1.86 | 0.74 |
| 3/4” | 0.94 | 3.22 | 2.69 | 1.07 |
| 1” | 1.27 | 4.36 | 3.63 | 1.45 |
| 1-1/4” | 1.79 | 6.13 | 5.11 | 2.04 |
| 1-1/2” | 2.16 | 7.40 | 6.16 | 2.47 |
| 2” | 2.92 | 10.00 | 8.33 | 3.33 |
| 2-1/2” | 3.59 | 12.32 | 10.27 | 4.11 |
| 3” | 4.66 | 15.97 | 13.31 | 5.32 |
| 4” | 6.44 | 22.09 | 18.41 | 7.36 |
| 5” | 8.42 | 28.87 | 24.06 | 9.62 |
| 6” | 10.38 | 35.59 | 29.66 | 11.86 |
| 8” | 14.40 | 49.36 | 41.13 | 16.45 |
| 10” | 18.74 | 64.25 | 53.54 | 21.42 |
| 12” | 22.93 | 78.61 | 65.51 | 26.20 |
| 14” | 25.58 | 87.70 | 73.08 | 29.23 |
| 16” | 29.95 | 102.67 | 85.56 | 34.22 |

| Nominal Pipe Size (inch) | Tee Run | Tee Branch | 90° Elbow | 45° Elbow |
| --- | --- | --- | --- | --- |
|  | f=0.35 | f=1.2 | f=1 | f=0.4 |
| 1/2” | 0.20 | 0.66 | 0.57 | 0.23 |
| 3/4” | 0.29 | 0.98 | 0.82 | 0.33 |
| 1” | 0.39 | 1.33 | 1.11 | 0.44 |
| 1-1/4” | 0.54 | 1.87 | 1.56 | 0.62 |
| 1-1/2” | 0.66 | 2.25 | 1.88 | 0.75 |
| 2” | 0.89 | 3.05 | 2.54 | 1.02 |
| 2-1/2” | 1.10 | 3.75 | 3.13 | 1.25 |
| 3” | 1.42 | 4.87 | 4.06 | 1.62 |
| 4” | 1.96 | 6.73 | 5.61 | 2.24 |
| 5” | 2.57 | 8.80 | 7.33 | 2.93 |
| 6” | 3.16 | 10.85 | 9.04 | 3.62 |
| 8” | 4.39 | 15.04 | 12.54 | 5.01 |
| 10” | 5.71 | 19.58 | 16.32 | 6.53 |
| 12” | 6.99 | 23.96 | 19.97 | 7.99 |
| 14” | 7.80 | 26.73 | 22.28 | 8.91 |
| 16” | 9.13 | 31.29 | 26.08 | 10.43 |

Engineering Data

| Di · θ |  | Clay Drainage Tile | 0.011-0.017 |
| --- | --- | --- | --- |
| 2 |  | Concret | 0.012-0.016 |
|  |  | Concrete Lined | 0.012-0.018 |

Fl

ow

H/Di

Hyd

rauli

c ra

dius

Velo

city

Engineering Data

Engineering Data

Engineering Data

Engineering Data

Engineering Data

|  |  |  | CPVC | 4120 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | PVC1 | 120 |  |  |

Expansion (inchs/Foot)

Expansion (mm/m)

CPV

C41

20

PV

C112

0

|  | Long straight sections | Straight sections 13 to 23 feet long | Straight sections 7 to 13 feet long | Straight sections 7 feet or less |
| --- | --- | --- | --- | --- |
| Absorbing expansion and contraction in straight sections | In accordance with the method of absorbing expansion and contraction in bending sections | In accordance with the method of absorbing expansion and contraction in bending sections | Adjusting for expansion and contraction is not necessary. |
| Absorbing expansion and contraction in bending sections |  |  | Using an elbow |
| Locaiton branch points on the main pipe and absorbing expansion and contrac- tion in the branch sections. | Long distance from anchored point to branch point | Distance of 13' to 23' from anchored point to branch point | Distance of 7' to 13' from anchored point to branch point |  |
|  | Usage of 3 pcs of elbow | Usage of 1 pc. of bend and 1 pc.of elbow | Usage of 2 pcs of elbow | Adjusting for expansion and contraction is not necessary |
|  |  | (Remarks) Be sure to use bend on the main pipe side |  |  |
| Location of branch | Branch as near as possible to anchored points. |

Engineering Data

|  | Long straight sections | Straight sections 13 to 23 feet long | Straight sections 7 to 13 feet long | Straight sections 7 feet or less |
| --- | --- | --- | --- | --- |
| Absorbing expansion and contraction in straight sections | In accordance with the method of absorbing expansion and contraction in bending sections | In accordance with the method of absorbing expansion and contraction in bending sections | Adjusting for expansion and contraction is not necessary. |
| Absorbing expansion and contraction in bending sections |  |  | Using an elbow |
| Locaiton branch points on the main pipe and absorbing expansion and contrac- tion in the branch sections. | Long distance from anchored point to branch point | Distance of 13˚ to 23˚ from anchored point to branch point | Distance of 7˚ to 13˚ from anchored point to branch point |  |
|  | Usage of 3 pcs of elbow | Usage of 1 pc. of bend and 1 pc.of elbow | Usage of 2 pcs of elbow | Adjusting for expansion and contraction is not necessary |
|  |  | (Remarks) Be sure to use bend on the main pipe side |  |  |
| Location of branch | Branch as near as possible to anchored points. |

Engineering Data

Engineering Data

Engineering Data

| Nominal Pipe Size | Schedule 80 PVC | Schedule 80 CPVC |
| --- | --- | --- |
|  | 60°F | 80°F | 100°F | 120°F | 140°F | 80°F | 100°F | 120°F | 140°F | 160°F | 180°F | 200°F |
| inch | mm | Recommended Support Spacing (feet) | Recommended Support Spacing (feet) |
| 1/2” | 21.34 | 4.4 | 4.3 | 4.2 | 4.1 | 4.0 | 4.1 | 4.0 | 3.9 | 3.8 | 3.7 | 3.6 | 3.5 |
| 3/4” | 26.67 | 4.8 | 4.7 | 4.6 | 4.5 | 4.4 | 4.5 | 4.4 | 4.3 | 4.2 | 4.1 | 4.0 | 3.9 |
| 1” | 33.40 | 5.3 | 5.2 | 5.1 | 5.0 | 4.8 | 5.0 | 4.9 | 4.8 | 4.7 | 4.6 | 4.4 | 4.3 |
| 1-1/4” | 42.16 | 5.9 | 5.8 | 5.7 | 5.5 | 5.3 | 5.5 | 5.4 | 5.3 | 5.2 | 5.0 | 4.9 | 4.7 |
| 1-1/2” | 48.26 | 6.2 | 6.1 | 6.0 | 5.9 | 5.6 | 5.8 | 5.7 | 5.6 | 5.5 | 5.3 | 5.2 | 5.0 |
| 2” | 60.33 | 6.8 | 6.7 | 6.6 | 6.4 | 6.2 | 6.4 | 6.3 | 6.1 | 6.0 | 5.8 | 5.7 | 5.5 |
| 2-1/2” | 73.03 | 7.5 | 7.4 | 7.3 | 7.1 | 6.8 | 7.1 | 6.9 | 6.8 | 6.7 | 6.5 | 6.3 | 6.1 |
| 3” | 88.90 | 8.2 | 8.0 | 7.9 | 7.7 | 7.4 | 7.7 | 7.5 | 7.4 | 7.2 | 7.0 | 6.8 | 6.6 |
| 4” | 114.30 | 9.1 | 8.9 | 8.8 | 8.6 | 8.2 | 8.5 | 8.4 | 8.2 | 8.0 | 7.8 | 7.6 | 7.3 |
| 5” | 141.30 | 9.9 | 9.8 | 9.6 | 9.4 | 9.0 | 9.3 | 9.2 | 9.0 | 8.8 | 8.5 | 8.3 | 8.0 |
| 6” | 168.28 | 10.8 | 10.6 | 10.4 | 10.2 | 9.8 | 10.1 | 9.9 | 9.7 | 9.5 | 9.3 | 9.0 | 8.7 |
| 8” | 219.08 | 12.0 | 11.8 | 11.6 | 11.3 | 10.9 | 11.3 | 11.1 | 10.9 | 10.6 | 10.3 | 10.1 | 9.7 |
| 10” | 273.05 | 13.3 | 13.1 | 12.8 | 12.5 | 12.1 | 12.5 | 12.3 | 12.0 | 11.8 | 11.4 | 11.1 | 10.8 |
| 12” | 323.85 | 14.4 | 14.2 | 13.9 | 13.6 | 13.1 | 13.6 | 13.3 | 13.0 | 12.8 | 12.4 | 12.1 | 11.7 |
| 14” | 355.60 | 15.1 | 14.8 | 14.6 | 14.2 | 13.7 | 14.2 | 14.0 | 13.7 | 13.4 | 13.0 | 12.6 | 12.2 |
| 16” | 406.40 | 16.1 | 15.8 | 15.5 | 15.2 | 14.6 | 15.2 | 14.9 | 14.6 | 14.2 | 13.9 | 13.5 | 13.0 |
| 18” | 457.20 | 17.0 | 16.7 | 16.4 | 16.1 | 15.5 | 16.0 | 15.7 | 15.4 | 15.1 | 14.7 | 14.2 | 13.8 |
| 20” | 508.00 | 17.9 | 17.6 | 17.3 | 16.9 | 16.3 | 16.9 | 16.6 | 16.2 | 15.9 | 15.0 | 15.4 | 14.5 |
| 24” | 609.60 | 19.6 | 19.2 | 18.9 | 18.5 | 17.8 | 18.4 | 18.1 | 17.7 | 17.3 | 16.4 | 16.8 | 15.8 |

Engineering Data

| Adj. Swivel Ring Split ring type Fig. 1 2/4 to 8 in. pipe | Split Ring Fig. 2 3/6 to 8 in. pipe |
| --- | --- |
| Adj. Ring Fig. 6 ½ to 8 in. pipe | Adj.Swivel Ring Fig. 7 ½ to 8 in. pipe |
| Adj. Clevis-Standard Fig. 11 ½ to 30 in. pipe | Adj. Clevis For Insulated Lines Fig. 12 3/4 to 8 in. pipe |

| Adj.Steel Yoke Pipe Roll Fig. 3 2½ to 20 in. pipe | Adj. Swivel Pipe Roll Fig. 4 2½ to 12 in. pipe |
| --- | --- |
| Single Pipe Roll Fig. 8 1 to 30 in. pipe | Adj. Pipe Roll Support Fig. 9 1 to 30 in. pipe |
| Roller Chair Fig. 13 2 to 12 in. pipe | Pipe Roll and Plate Fig. 14 2 to 24 in pipe |
| Pipe Roll Stand Complete Fig. 16 2 to 42 in. pipe |  |

Wrought Strap Short Fig. 5 ½ to 4 in. pipe

One Hole Clamp Fig. 10 3/6 to 4 in. pipe

Tin Strap Fig. 15 ¼ to 2 in. pipe

Engineering Data

| Pipe Clamp Medium Fig. 17 ½ to 24 in. pipe | Double Bolt Pipe Clamp Fig. 18 2/4 to 36 in. pipe |
| --- | --- |

Insulation Protection Shield Fig. 19

½ to 24 in. pipe

U Bolt Fig. 20"

Standard

½ to 30 in. pipe Light weight

½ to 10 in. pipe

4

Installation

Installation

Max 8 feet (2.5m)

Max 8 feet (2.5m)

! WARNING

! WARNING

Failure to follow the safety precautions below may result in misapplication or improper installation and testing which can cause severe personal injury and/

or property damage.

Installation

NEVER use compressed air or gas in PVC/CPVC pipe and ﬁttings.

NEVER test PVC/CPVC pipe and ﬁttings with com- pressed air or gas, or air-over-water boosters.w ONLY use PVC/CPVC pipe for water and approved

chemicals.

Installation

②

Installation

Installation

Installation

! WARNING

Failure to follow the safety precautions below may result in misapplication or improper installation and testing which can cause severe personal injury and/or

property damage.

! CAUTION

Installation

“CAUTION” identiﬁes hazards or unsafe practices which can result in minor injury or product or property damage if instructions, including recommended pre-

cautions, are not followed.

Installation

Installation

| Pipe | Threads |
| --- | --- |
| Nominal Size | Outside Diameter D | Number of Threads Per Inch | Normal Engage- ment By Hand C | Length of Effective Thread A | Total Length : End of pipe to vanish point B | Pitch Diameter at end of Internal Thread E | Depth of Thread (Max.) |
|  | inch | mm |  | inch | mm | inch | mm | inch | mm | inch | mm | inch | mm |
| 1/2" | 0.840 | 21.34 | 14.0 | 0.320 | 4.48 | 0.5337 | 7.47 | 0.7815 | 10.94 | 0.77843 | 19.772 | 0.05714 | 1.451 |
| 3/4" | 1.050 | 26.67 | 14.0 | 0.339 | 4.75 | 0.5457 | 7.64 | 0.7935 | 11.11 | 0.98887 | 25.117 | 0.05714 | 1.451 |
| 1" | 1.315 | 33.40 | 11.5 | 0.400 | 4.60 | 0.6828 | 7.85 | 0.9845 | 11.32 | 1.23863 | 31.461 | 0.06957 | 1.767 |
| 1-1/4" | 1.660 | 42.16 | 11.5 | 0.420 | 4.83 | 0.7068 | 8.13 | 1.0085 | 11.60 | 1.58338 | 40.218 | 0.06957 | 1.767 |
| 1-1/2" | 1.900 | 48.26 | 11.5 | 0.402 | 4.83 | 0.7235 | 8.32 | 1.0252 | 11.79 | 1.82234 | 46.287 | 0.06957 | 1.767 |
| 2" | 2.375 | 60.33 | 11.5 | 0.436 | 5.01 | 0.7565 | 8.70 | 1.0582 | 12.17 | 2.29627 | 58.325 | 0.06957 | 1.767 |
| 2-1/2" | 2.875 | 73.03 | 8.0 | 0.682 | 5.46 | 1.1375 | 9.10 | 1.5712 | 12.57 | 2.76215 | 70.159 | 0.10000 | 2.540 |
| 3" | 3.500 | 88.90 | 8.0 | 0.766 | 6.13 | 1.2000 | 9.60 | 1.6337 | 13.07 | 3.38850 | 86.068 | 0.10000 | 2.540 |
| 4" | 4.500 | 114.30 | 8.0 | 0.844 | 6.75 | 1.3000 | 10.40 | 1.7337 | 13.87 | 4.38712 | 111.433 | 0.10000 | 2.540 |

Installation

! CAUTION

- Do not over-torque flange bolts.

- Use the proper bolt tightening sequence.

- Make sure the system is in proper alignment.

- Flanges should not be used to draw piping assem- blies together.

- Flat washers must be used under every nut and bolt

head.

| Pipe Size (IPS) | No. Bolt Holes | Bolt Diameter | Approx. Bolt Length* in. | Recommended Torque ft./lbs. |
| --- | --- | --- | --- | --- |
| 1/2 | 4 | 1/2 | 2 1/2 | 10-15 |
| 3/4 | 4 | 1/2 | 2 1/2 | 10-15 |
| 1 | 4 | 1/2 | 2 1/2 | 10-15 |
| 1 1/4 | 4 | 1/2 | 3 | 10-15 |
| 1 1/2 | 4 | 1/2 | 3 | 10-15 |
| 2 | 4 | 5/8 | 3 1/2 | 20-30 |
| 2 1/2 | 4 | 5/8 | 3 | 20-30 |
| 3 | 4 | 5/8 | 3 1/2 | 20-30 |
| 4 | 8 | 5/8 | 4 | 20-30 |
| 6 | 8 | 3/4 | 4 | 33-50 |
| 8 | 8 | 7/8 | 5 | 33-50 |
| 10 | 12 | 7/8 | 5 | 53-75 |
| 12 | 12 | 7/8 | 5 | 53-75 |

5

|  | Abbreviation | Material |
| --- | --- | --- |
| Plastic | PVC | Polyvinyl Chloride (Unplasticized Polyvinyl Chloride) |
|  | CPVC | Chlorinated Polyvinyl Chloride |
|  | PP | Polypropylene |
|  | PVDF | Polyvinylidene Fluoride |
|  | PTFE | Polytetrafluoroethylene |
| Rubber | EPDM | Ethylene Propylene diene Methylene |
|  | FKM | Fluoro Rubber or Fluorocarbon Rubber |

Chemical Resistance

Chemical Resistance

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Acetaldehyde CH3CHO | Pure | 20 | 68 | -- | -- | ++ | -- | ++ | + | -- |
|  |  | 40 | 104 |  |  | ++ |  | ++ |  |  |
|  |  | 60 | 140 |  |  | + |  | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Acetamide CH3CONH2 | Satu | 20 | 68 |  |  | ++ |  | ++ | ++ | ++ |
|  |  | 40 | 104 |  |  |  |  | ++ | ++ | ++ |
|  |  | 60 | 140 |  |  |  |  | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Acetic acid CH3COOH | 10 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | + |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | + |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | + | - |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | - | -- |
|  |  | 100 | 212 |  |  |  | + | ++ |  |  |
|  |  | 120 | 248 |  |  |  | + | ++ |  |  |
| Acetic acid CH3COOH | 20 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | + |
|  |  | 40 | 104 | + | ++ | ++ | ++ | ++ | ++ | - |
|  |  | 60 | 140 | - | + | + | ++ | ++ | + | - |
|  |  | 80 | 176 |  | - | - | ++ | ++ |  | -- |
|  |  | 100 | 212 |  |  |  | + | ++ |  |  |
|  |  | 120 | 248 |  |  |  | - | ++ |  |  |
| Acetic acid CH3COOH | 50 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | -- | + |
|  |  | 40 | 104 | + | + | + | ++ | ++ |  | - |
|  |  | 60 | 140 | - | - | - | ++ | ++ |  | -- |
|  |  | 80 | 176 |  | -- |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | + | ++ |  |  |
|  |  | 120 | 248 |  |  |  | - | ++ |  |  |
| Acetic acid CH3COOH | 80 | 20 | 68 | ++ | + | + | ++ | ++ | -- | - |
|  |  | 40 | 104 | + | - | - | ++ | ++ |  |  |
|  |  | 60 | 140 | - | -- | -- | + | ++ |  |  |
|  |  | 80 | 176 |  |  |  | + | ++ |  |  |
|  |  | 100 | 212 |  |  |  | - | ++ |  |  |
|  |  | 120 | 248 |  |  |  | -- | ++ |  |  |
| Acetic anhydride (CH3CO)2O | Pure | 20 | 68 | -- | -- | + | + | ++ | - | -- |
|  |  | 40 | 104 |  |  | - | - | ++ | -- |  |
|  |  | 60 | 140 |  |  | -- | -- | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Acetone CH3COCH3 | Pure | 20 | 68 | -- | -- | ++ | - | ++ | + | -- |
|  |  | 40 | 104 |  |  | ++ | -- | ++ | + |  |
|  |  | 60 | 140 |  |  | - |  | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Acetonitrile CH3CN |  | 20 | 68 | -- | -- | + | - | ++ | + | - |
|  |  | 40 | 104 |  |  |  |  | ++ |  |  |
|  |  | 60 | 140 |  |  |  |  | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Acetophenone C6H5COCH3 |  | 20 | 68 | -- | -- | ++ | ++ | ++ | ++ | -- |
|  |  | 40 | 104 |  |  | + | - | ++ | ++ |  |
|  |  | 60 | 140 |  |  | - | -- | ++ | ++ |  |
|  |  | 80 | 176 |  |  | -- |  | ++ | + |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Acetyl acetone CH3COCH2COCH3 |  | 20 | 68 | -- | -- |  | -- | ++ |  |  |
|  |  | 40 | 104 |  |  |  |  |  |  |  |
|  |  | 60 | 140 |  |  |  |  |  |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Acetyl bromide CH3COBr |  | 20 | 68 |  |  |  | ++ | ++ |  |  |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | + | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Acetyl chloride CH3COCl |  | 20 | 68 |  |  | ++ | ++ | ++ | -- | + |
|  |  | 40 | 104 |  |  | ++ | + | ++ |  |  |
|  |  | 60 | 140 |  |  | - | - | ++ |  |  |
|  |  | 80 | 176 |  |  | -- | -- | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Acetylene C2H2 |  | 20 | 68 | -- | -- | ++ | ++ | ++ | - | ++ |
|  |  | 40 | 104 |  |  | ++ | ++ | ++ | - | ++ |
|  |  | 60 | 140 |  |  | ++ | ++ | ++ | -- | ++ |
|  |  | 80 | 176 |  |  | + | ++ | ++ |  | ++ |
|  |  | 100 | 212 |  |  |  |  | ++ |  | + |
|  |  | 120 | 248 |  |  |  |  | + |  |  |
| Acrylonitrile CH2=CHCN |  | 20 | 68 | -- | -- | + | ++ | ++ | ++ | -- |
|  |  | 40 | 104 |  |  | - | + | ++ | ++ |  |
|  |  | 60 | 140 |  |  |  | - | ++ | + |  |
|  |  | 80 | 176 |  |  |  | -- | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Adipic acid Aqueous | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | + | ++ | ++ | + | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ | + | + |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Allyl alcohol CH2=CHCH2OH |  | 20 | 68 | -- | -- | ++ | ++ | ++ |  | ++ |
|  |  | 40 | 104 |  |  | ++ | ++ | ++ |  | ++ |
|  |  | 60 | 140 |  |  | + | ++ | ++ |  | ++ |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  | + |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | + |  |  |
| Allyl chloride CH2=CHCH2Cl |  | 20 | 68 | -- |  |  | ++ | ++ | -- | + |
|  |  | 40 | 104 |  |  |  | - | ++ |  | + |
|  |  | 60 | 140 |  |  |  | -- | ++ |  | - |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Alminium Ammonium sulfate (Ammonium alum) (NH4)2SO4Al2(SO4)3 | Satu | 20 | 68 |  |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 |  |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 |  |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Alum(Potassium alum) K2SO4Al2(SO4)324H2O | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | + | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ | + | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Aluminium acetate (CH3COO)3Al | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | + | + | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 |  |  |  | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  |  | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Aluminium bromide AlBr3 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ |  | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Aluminium chloride AlCl3 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | + | + | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ | + | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Aluminium fluoride AlF3 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |

Chemical Resistance

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Aluminium hydroxide Al(OH)3 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | + | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ | + | + |
|  |  | 120 | 248 |  |  |  | ++ |  |  |  |
| Aluminium nitrate Al(NO3)3 · 9H2O | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ | + | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Aluminium sulfate Al2(SO4)3 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Amber acid (Succinic acid) COOH(CH2)2COOH | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | + | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ | ++ | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Aminoacetic acid NH2CH2COOH | 10 | 20 | 68 | ++ |  | ++ | ++ | ++ | ++ | + |
|  |  | 40 | 104 | ++ |  | ++ | ++ | ++ | ++ |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Ammonia gas NH3 | 100 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | -- |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ |  |
|  |  | 60 | 140 | ++ | + | + | ++ | ++ | ++ |  |
|  |  | 80 | 176 |  | - | + | ++ | ++ | + |  |
|  |  | 100 | 212 |  |  |  | + | ++ | - |  |
|  |  | 120 | 248 |  |  |  | + | ++ |  |  |
| Ammonia liquid NH3 | 100 | 20 | 68 | - | - | ++ | ++ | ++ | ++ | - |
|  |  | 40 | 104 | -- | -- | + | ++ | ++ | + |  |
|  |  | 60 | 140 |  |  | - | ++ | ++ | + |  |
|  |  | 80 | 176 |  |  | -- | ++ | ++ | - |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ | - |  |
|  |  | 120 | 248 |  |  |  | + | ++ |  |  |
| Ammonia water NH3Aq | 10 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | + |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | - |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | -- |
|  |  | 80 | 176 |  | + | + | ++ | ++ | ++ |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ | ++ |  |
|  |  | 120 | 248 |  |  |  | + | ++ |  |  |
| Ammonia water NH3Aq | 40 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | - |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | - |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | -- |
|  |  | 80 | 176 |  |  | ++ | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | + | ++ |  |  |
| Ammonium phosphate |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Ammonium acetate CH3COONH4 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | + | ++ | ++ | + | + |
|  |  | 100 | 212 |  |  |  | ++ | ++ | + | + |
|  |  | 120 | 248 |  |  |  | + | ++ |  |  |
| Ammonium carbonate (NH4)2CO3 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ | + | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Ammonium chloride NH4Cl | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | + | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  | + | ++ | ++ | + | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Ammonium fluoride NH4F | 20 | 20 | 68 | ++ |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | + |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | -- |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  | + | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Ammonium hydrogen carbonate NH4HCO3 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  | ++ | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Ammonium hydrogendifluoride NH4HF2 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | + | + |
|  |  | 100 | 212 |  |  |  | ++ | ++ | + | + |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Ammonium metaphosphate NH4PO3 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Ammonium nitrate NH4NO3 |  | 20 | 68 | + | + | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | + | + | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | + | + | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Ammonium perchlorate NH4ClO4 | 10 | 20 | 68 | ++ |  | ++ |  | ++ |  |  |
|  |  | 40 | 104 | ++ |  | ++ |  | ++ |  |  |
|  |  | 60 | 140 | ++ |  | ++ |  | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Ammonium sulfate (NH4)2SO4 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Ammonium sulfide (NH4)2S |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 |  |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 |  |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Ammonium sulfite (NH4)2SO3 |  | 20 | 68 | ++ |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Amyl acetate CH3CO2(CH2)4CH3 | Pure | 20 | 68 | -- | -- | -- | ++ | ++ | -- | -- |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | + | ++ |  |  |
|  |  | 80 | 176 |  |  |  | + |  |  |  |
|  |  | 100 | 212 |  |  |  | - |  |  |  |
|  |  | 120 | 248 |  |  |  | -- |  |  |  |
| Amyl alcohol C5H11OH | Pure | 20 | 68 | ++ | ++ | ++ | ++ | ++ | - | - |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ |  |  |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ |  |  |
|  |  | 80 | 176 |  | + | + | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |

Chemical Resistance

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Amyl chloride CH3 (CH2) 4Cl | Pure | 20 | 68 | -- | -- | -- | ++ | ++ | -- | + |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Aniline C6H5NH2 | Pure | 20 | 68 | - | - | + | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | -- | -- | + | + | ++ | - | + |
|  |  | 60 | 140 |  |  | - | + | ++ | -- | - |
|  |  | 80 | 176 |  |  | -- | - | ++ |  |  |
|  |  | 100 | 212 |  |  |  | -- | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Aniline hydrochloride C6H5NH2 · HCl | Pure | 20 | 68 | + |  |  | ++ | ++ |  | ++ |
|  |  | 40 | 104 | + |  |  | ++ | ++ |  | ++ |
|  |  | 60 | 140 | - |  |  | + | ++ |  | ++ |
|  |  | 80 | 176 |  |  |  | -- | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Animal oil(Lard) |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Antimony trichloride SbCl3 | Satu | 20 | 68 | ++ | -- | ++ | -- | ++ | + | ++ |
|  |  | 40 | 104 | ++ |  | ++ |  | ++ |  | ++ |
|  |  | 60 | 140 | + |  | + |  | + |  | ++ |
|  |  | 80 | 176 |  |  | + |  | + |  | + |
|  |  | 100 | 212 |  |  |  |  | + |  |  |
|  |  | 120 | 248 |  |  |  |  | + |  |  |
| Aque regia 3HCl+HNO3 |  | 20 | 68 | - | - | - | ++ | ++ | -- | - |
|  |  | 40 | 104 | - | - | - | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  | -- | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | + | ++ |  |  |
|  |  | 120 | 248 |  |  |  | - | + |  |  |
| Arsenic acid H3AsO4 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | + | + | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | - | + | + | ++ | ++ | + | ++ |
|  |  | 80 | 176 |  | - | - | ++ | ++ | + | + |
|  |  | 100 | 212 |  |  |  | + | ++ |  | + |
|  |  | 120 | 248 |  |  |  | - | ++ |  |  |
| Asphalt |  | 20 | 68 | -- | -- | ++ | ++ | ++ | -- | ++ |
|  |  | 40 | 104 |  |  | ++ | ++ | ++ |  | ++ |
|  |  | 60 | 140 |  |  | ++ | ++ | ++ |  | ++ |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Balium sulfate BaSO4 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Balium sulfide BaS | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ |  | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Barium carbonate BaCO3 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  | ++ |
| Barium chloride BaCl2 · 2H2O | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  | ++ |

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Barium hydroxide Ba(OH)2 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ | + | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  | ++ |
| Barium nitrate Ba(NO3)2 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ | + | ++ |
|  |  | 120 | 248 |  |  |  | ++ |  |  | ++ |
| Beer |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Beet suger liquors |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ |  | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Benzaldehyde C6H5CHO | 10 | 20 | 68 | -- | -- | - | + | ++ | + | - |
|  |  | 40 | 104 |  |  |  | - | ++ |  |  |
|  |  | 60 | 140 |  |  |  |  | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Benzene C6H6 | Pure | 20 | 68 | - | - | + | ++ | ++ | -- | + |
|  |  | 40 | 104 | -- | -- | - | + | ++ |  | + |
|  |  | 60 | 140 |  |  |  | + | ++ |  | + |
|  |  | 80 | 176 |  |  |  | + | ++ |  | + |
|  |  | 100 | 212 |  |  |  | - | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Benzensulfonic acid C6H5SO3H |  | 20 | 68 | -- | -- | -- | + | ++ |  | ++ |
|  |  | 40 | 104 |  |  |  | + | ++ |  | ++ |
|  |  | 60 | 140 |  |  |  | - | ++ |  | ++ |
|  |  | 80 | 176 |  |  |  | - | ++ |  |  |
|  |  | 100 | 212 |  |  |  | -- | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | + |  |  |
| Benzine | Pure | 20 | 68 | -- | -- | ++ | ++ | ++ | -- | ++ |
|  |  | 40 | 104 |  |  | + | ++ | ++ |  | ++ |
|  |  | 60 | 140 |  |  | - | + | ++ |  | + |
|  |  | 80 | 176 |  |  |  |  | ++ |  | + |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Benzoic acid C6H5COOH | Pure | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | + | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | + | + | - | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | - | -- | ++ | ++ | + | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | + |
|  |  | 120 | 248 |  |  |  | + |  |  |  |
| Benzyl alcohol C8H5CH2OH | Pure | 20 | 68 |  |  | ++ | ++ | ++ | ++ | - |
|  |  | 40 | 104 |  |  | ++ | ++ | ++ | + |  |
|  |  | 60 | 140 |  |  | ++ | ++ | ++ | + |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ | - |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Benzyl benzoate C6H5COOCH2C6H5 | Satu | 20 | 68 |  |  |  | ++ | ++ | + |  |
|  |  | 40 | 104 |  |  |  |  |  |  |  |
|  |  | 60 | 140 |  |  |  |  |  |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Benzyl chloride C6H5CH2Cl | Pure | 20 | 68 |  |  | ++ | ++ | ++ | -- | + |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  | - |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  | -- |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |

Chemical Resistance

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Bleaching liquor Ca(ClO)2 | 5 | 20 | 68 | ++ | ++ |  | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ |  | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Bleaching liquor Ca(ClO)2 | 12 | 20 | 68 | ++ | ++ |  | ++ | ++ | + | ++ |
|  |  | 40 | 104 | ++ | ++ |  | ++ | ++ |  |  |
|  |  | 60 | 140 | ++ | ++ |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Borax Na2B4O7 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ |  | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Boric acid H3BO3 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | ++ | ++ | ++ | + | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | + |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Boron trichloride BCl3 |  | 20 | 68 | ++ |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  | ++ | ++ | ++ |  | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Brine |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | + | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | + |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Bromic acid HBrO3 | Pure | 20 | 68 | ++ | ++ | -- | ++ | ++ |  |  |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | + | ++ |  |  |
| Bromine vapor | 25 | 20 | 68 | + |  | -- | ++ | ++ | -- | ++ |
|  |  | 40 | 104 | - |  |  | ++ | ++ |  | ++ |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  | ++ |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | + | ++ |  |  |
|  |  | 120 | 248 |  |  |  | + | ++ |  |  |
| Bromine water | Satu | 20 | 68 | + | - | - | ++ | ++ | -- | ++ |
|  |  | 40 | 104 | - |  | -- | ++ | ++ |  | ++ |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | + | ++ |  |  |
|  |  | 100 | 212 |  |  |  | + | ++ |  |  |
|  |  | 120 | 248 |  |  |  | + | ++ |  |  |
| Butadiene CH2=CH-CH=CH2 | Gas | 20 | 68 | ++ | ++ |  | ++ | ++ | -- | ++ |
|  |  | 40 | 104 | ++ | ++ |  | ++ | ++ |  | ++ |
|  |  | 60 | 140 | ++ |  |  | ++ | ++ |  | ++ |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Butane CH3(CH2)2CH3 | Gas | 20 | 68 | ++ | ++ | ++ | ++ | ++ | -- | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ |  | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ |  | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ |  | ++ |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Butyl acetate CH3COOC4H9 | Pure | 20 | 68 | - | - | - | ++ | ++ | - | -- |
|  |  | 40 | 104 | -- | -- | -- | + | ++ | - |  |
|  |  | 60 | 140 |  |  |  | -- | ++ | -- |  |
|  |  | 80 | 176 |  |  |  |  | + |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Butyl acrylate CH2CHCOOC4H9 | Pure | 20 | 68 | -- | -- | -- | ++ | ++ | ++ | -- |
|  |  | 40 | 104 |  |  |  | + | ++ | ++ |  |
|  |  | 60 | 140 |  |  |  | - | ++ |  |  |
|  |  | 80 | 176 |  |  |  | -- |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Butyl alcohol C4H9OH | Pure | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | + |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | + |
|  |  | 60 | 140 | + | ++ | ++ | ++ | ++ | + | - |
|  |  | 80 | 176 |  | + | ++ | ++ | ++ | - |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Butyl amine CH3(CH2)3NH2 | Satu | 20 | 68 | -- | -- | -- | + | ++ | -- | -- |
|  |  | 40 | 104 |  |  |  | -- | ++ |  |  |
|  |  | 60 | 140 |  |  |  |  | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Butyl bromide CH3(CH2)3Br | Pure | 20 | 68 |  |  |  | ++ | ++ |  |  |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Butyl carbitol O CH2CH2OC4H9 CH2CH2OH |  | 20 | 68 |  |  |  | ++ | ++ | ++ |  |
|  |  | 40 | 104 |  |  |  |  |  |  |  |
|  |  | 60 | 140 |  |  |  |  |  |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Butyl celloxolve C4H9O(CH2)2OH | Pure | 20 | 68 |  |  |  | ++ | ++ |  | -- |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | + | ++ |  |  |
|  |  | 80 | 176 |  |  |  | - | ++ |  |  |
|  |  | 100 | 212 |  |  |  | -- |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Butyl chloride CH3(CH2)3Cl |  | 20 | 68 | -- | -- | -- | ++ | ++ | - | + |
|  |  | 40 | 104 |  |  |  | ++ | ++ | -- | - |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Butyl ether [CH3(CH2)3]2O |  | 20 | 68 | -- | -- | -- | ++ | ++ | -- | -- |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | - | ++ |  |  |
|  |  | 80 | 176 |  |  |  | -- |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Butyl mercaptan CH3(CH2)3SH | Pure | 20 | 68 |  |  |  | ++ | ++ |  |  |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Butyl phenol C6H4(OH)(C4H9) |  | 20 | 68 | - | - | ++ | ++ | ++ | -- | - |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Butyl phthalate C6H4(COOC4H9)(COOH) |  | 20 | 68 |  |  | ++ | ++ | ++ | + | + |
|  |  | 40 | 104 |  |  | ++ | + | ++ |  | + |
|  |  | 60 | 140 |  |  | ++ | - |  |  | -- |
|  |  | 80 | 176 |  |  |  | -- |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Butyl stearate C17H35COOC4H9 | Pure | 20 | 68 |  |  |  | ++ | ++ | - | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  | ++ |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  | ++ |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |

Chemical Resistance

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Butylene CH3CH2CH=CH2 |  | 20 | 68 |  |  |  | ++ | ++ |  | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  | ++ |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  | ++ |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  | + |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Butynediol HOCH2C ≡ CCH2OH |  | 20 | 68 | + |  |  | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | - |  |  | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 |  |  |  | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Butyric acid CH3CH2CH2COOH | Pure | 20 | 68 | + | + | ++ | ++ | ++ | - | - |
|  |  | 40 | 104 |  |  | ++ | ++ | ++ | -- | -- |
|  |  | 60 | 140 |  |  | ++ | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  | ++ | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Caffeine citrate |  | 20 | 68 |  |  |  | ++ | ++ |  |  |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Calcium acetate Ca(CH3COO)2 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | + | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | + | ++ |  |  |
| Calcium bromide CaBr2 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Calcium carbonate CaCO3 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ |  | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  | ++ |
| Calcium chlorate Ca(ClO3)22H2O | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Calcium chloride CaCl2 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Calcium hydrogen sulfite Ca(HSO3)2 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | + | ++ |
|  |  | 60 | 140 |  | ++ | ++ | ++ | ++ |  | ++ |
|  |  | 80 | 176 |  |  | ++ | ++ | ++ |  | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Calcium hydroxide Ca(OH)2 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  | + | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Calcium hypochlorite Ca(ClO)2 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | + | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | + | ++ |
|  |  | 60 | 140 | + | + | + | ++ | ++ | - | ++ |
|  |  | 80 | 176 |  | - | - | ++ | ++ | - | + |
|  |  | 100 | 212 |  |  |  | + | ++ |  | - |
|  |  | 120 | 248 |  |  |  |  |  |  |  |

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Calcium nitrate Ca(NO3)2 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Calcium sulfate CaSO4 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Calcium sulfide CaS | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ |  |  |  |
| Cane suger liquor |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Caprylic acid CH3(CH2)6COOH | Pure | 20 | 68 |  |  |  | ++ | ++ |  |  |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Carbitol HOC2H4OC2H4OC2H5 | Pure | 20 | 68 | ++ |  |  |  | ++ | ++ | ++ |
|  |  | 40 | 104 | + |  |  |  | ++ |  | + |
|  |  | 60 | 140 |  |  |  |  | ++ |  | - |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Carbon dioxide CO2 | Wet · Dry | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ | + | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Carbon disulfide CS2 | Pure | 20 | 68 | - | - | -- | ++ | ++ | -- | ++ |
|  |  | 40 | 104 | - | - |  |  | ++ |  | + |
|  |  | 60 | 140 | -- | -- |  |  | ++ |  | - |
|  |  | 80 | 176 |  |  |  |  | ++ |  | -- |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Carbon monoxide CO | Gas | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ |  | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Carbon tetrachloride CCl4 | Pure | 20 | 68 | -- | -- | -- | ++ | ++ | -- | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  | + |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  | + |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Carbonic acid H2CO3 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | + | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | + |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Casein |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 |  |  |  | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  |  | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |

Chemical Resistance

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Castor oil | Pure | 20 | 68 | ++ | ++ | ++ | ++ | ++ | + | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ |  | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ |  | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Caustic potash (Potassium hydroxide) KOH | 14 | 20 | 68 | + | + |  |  |  |  |  |
|  |  | 40 | 104 | + | -- |  |  |  |  |  |
|  |  | 60 | 140 | + | -- |  |  |  |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Caustic potash (Potassium hydroxide) KOH | 25 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | -- |
|  |  | 40 | 104 | ++ | + | ++ | ++ | ++ | ++ |  |
|  |  | 60 | 140 | ++ | + | ++ | + | ++ | ++ |  |
|  |  | 80 | 176 |  | + | ++ | - | ++ | ++ |  |
|  |  | 100 | 212 |  |  |  | -- | ++ | + |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Chloric acid HClO3 | 20 | 20 | 68 | ++ |  | -- | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 | + |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Chlorine dioxide ClO2 | Pure | 20 | 68 | - | - | - | ++ | ++ | - | + |
|  |  | 40 | 104 | -- | -- | -- | ++ | ++ |  |  |
|  |  | 60 | 140 | -- | -- |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Chlorine gas Cl2 | Wet | 20 | 68 | + | + | -- | ++ | ++ | -- | -- |
|  |  | 40 | 104 | - | - |  | ++ | ++ |  |  |
|  |  | 60 | 140 | - | - |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  | - |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Chlorine gas Cl2 | Dry | 20 | 68 | ++ | ++ | -- | ++ | ++ | -- | + |
|  |  | 40 | 104 | ++ | ++ |  | ++ | ++ |  | - |
|  |  | 60 | 140 | ++ | ++ |  | ++ | ++ |  | -- |
|  |  | 80 | 176 |  | ++ |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Chlorine water Cl2Aq | 400 ppm | 20 | 68 | ++ | ++ | - | ++ | ++ | - | + |
|  |  | 40 | 104 | ++ | ++ | -- | ++ | ++ | -- | - |
|  |  | 60 | 140 | - | + |  | ++ | ++ |  | -- |
|  |  | 80 | 176 |  | - |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Chloro benzene C6H5Cl | Pure | 20 | 68 | -- | -- | + | ++ | ++ | -- | + |
|  |  | 40 | 104 |  |  | - | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | + | ++ |  |  |
|  |  | 80 | 176 |  |  |  | - | ++ |  |  |
|  |  | 100 | 212 |  |  |  | - | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Chloro sulfonic acid SO2Cl(OH) | Pure | 20 | 68 | -- | -- | -- | - | ++ | -- | -- |
|  |  | 40 | 104 |  |  |  | -- | ++ |  |  |
|  |  | 60 | 140 |  |  |  |  | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Chloroacetic acid CH2ClCOOH | 50 | 20 | 68 | ++ | ++ | + | ++ | ++ | - | + |
|  |  | 40 | 104 | + | + | + | ++ | ++ |  | -- |
|  |  | 60 | 140 | + | + | -- | + | ++ |  |  |
|  |  | 80 | 176 |  |  |  | + | ++ |  |  |
|  |  | 100 | 212 |  |  |  | - | ++ |  |  |
|  |  | 120 | 248 |  |  |  | -- |  |  |  |
| Chloroform CHCl3 | pure | 20 | 68 | -- | -- | - | ++ | ++ | -- | - |
|  |  | 40 | 104 |  |  | -- | + | ++ |  |  |
|  |  | 60 | 140 |  |  |  | - | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Chromic acid H2CrO4 | 10 | 20 | 68 | ++ | ++ | -- | ++ | ++ | + | ++ |
|  |  | 40 | 104 | ++ | ++ |  | ++ | ++ | - | + |
|  |  | 60 | 140 | - | - |  | ++ | ++ | -- | + |
|  |  | 80 | 176 |  | -- |  | ++ | ++ |  | + |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | -- |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Chromic acid H2CrO4 | 20 | 20 | 68 | + | + | -- | ++ | ++ | + | + |
|  |  | 40 | 104 | - | - |  | ++ | ++ | -- | + |
|  |  | 60 | 140 | -- | -- |  | ++ | ++ |  | + |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  | - |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | -- |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Chromic acid H2CrO4 | 40 | 20 | 68 | + | + | -- | ++ | ++ | -- | + |
|  |  | 40 | 104 | - | - |  | ++ | ++ |  |  |
|  |  | 60 | 140 | -- | -- |  | - | ++ |  |  |
|  |  | 80 | 176 |  |  |  | -- | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Chromic acid H2CrO4 | 50 | 20 | 68 | - | - | -- | ++ | ++ | -- | + |
|  |  | 40 | 104 | -- | -- |  | - | ++ |  |  |
|  |  | 60 | 140 |  |  |  | -- | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | -- |  |  |
| Chromic acid H2CrO4 | 60 | 20 | 68 | -- | -- | -- | - | ++ | -- | -- |
|  |  | 40 | 104 |  |  |  | -- |  |  |  |
|  |  | 60 | 140 |  |  |  |  |  |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Chromium alum KCr(SO4)2 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 |  |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 |  |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  | ++ | ++ | ++ | + | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ | + | ++ |
|  |  | 120 | 248 |  |  |  | + |  |  |  |
| Citric acid C6H8O7 | 10 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | + | + | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | + | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ | + | ++ |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Coconut oil |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | + | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | + | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ |  | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Copper acetate Cu(CH3COO)2 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  | ++ |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Copper borofluoride CuBF4 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ | ++ |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ | ++ |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ | ++ |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ | + |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| copper carbonate CuCO3 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Copper chloride CuCl2 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ | + | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |

Chemical Resistance

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Copper cyanide CuCN |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 |  |  | ++ | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  | ++ | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  | + | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | + | ++ |  |  |
|  |  | 120 | 248 |  |  |  | - |  |  |  |
| Copper fluoride CuF | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | + | + | + | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | + |  |  |  |
| Copper sulfate CuSO4 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ | + | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Corn oil |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | + | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | + | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ |  | ++ |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Corn syrup |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ |  |  |  |
| Cottonseed oil |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | + | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | + | ++ |
|  |  | 80 | 176 |  |  | + | ++ | ++ | - | + |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | + |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  | + |
| Creosote |  | 20 | 68 | -- | -- | ++ | ++ | ++ | -- | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Cresol C6H4(CH3)OH | Pure | 20 | 68 | -- | -- | + | ++ | ++ | -- | + |
|  |  | 40 | 104 |  |  | - | ++ | ++ |  | + |
|  |  | 60 | 140 |  |  |  | + | ++ |  | + |
|  |  | 80 | 176 |  |  |  | + | ++ |  |  |
|  |  | 100 | 212 |  |  |  | - | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Croton aldehyde CH3CH=CHCHO | Pure | 20 | 68 | -- |  |  | ++ | ++ | + | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | + | ++ |  |  |
|  |  | 80 | 176 |  |  |  | + | ++ |  |  |
|  |  | 100 | 212 |  |  |  | - | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Cryolite Na3AlF6 |  | 20 | 68 | + | + | ++ | ++ |  |  |  |
|  |  | 40 | 104 | + | + | ++ | ++ |  |  |  |
|  |  | 60 | 140 | + | - | ++ | ++ |  |  |  |
|  |  | 80 | 176 |  | - | ++ | ++ |  |  |  |
|  |  | 100 | 212 |  |  |  | ++ |  |  |  |
|  |  | 120 | 248 |  |  |  | ++ |  |  |  |
| Cupric fluoride CuF22H2O | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  | + | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Cupric nitrate Cu(NO3)2 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | + | + | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  | + | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Cuprous chloride CuCl | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ | + | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Cyclohexane C6H12 | Pure | 20 | 68 | -- | -- | - | ++ | ++ | -- | ++ |
|  |  | 40 | 104 |  |  | -- | ++ | ++ |  | ++ |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  | + |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Cyclohexanol C6H11OH | Pure | 20 | 68 | -- | -- | ++ | ++ | ++ | - | ++ |
|  |  | 40 | 104 |  |  | + | ++ | ++ |  | ++ |
|  |  | 60 | 140 |  |  | - | + | ++ |  | + |
|  |  | 80 | 176 |  |  | -- | + | ++ |  |  |
|  |  | 100 | 212 |  |  |  | - | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Cyclohexanone C6H10O | Pure | 20 | 68 | -- | -- | - | ++ | ++ | -- | -- |
|  |  | 40 | 104 |  |  | -- | + | ++ |  |  |
|  |  | 60 | 140 |  |  |  | - | ++ |  |  |
|  |  | 80 | 176 |  |  |  | -- | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Decalin C10H18 | Pure | 20 | 68 |  |  | -- | ++ | ++ | -- | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Decane CH3(CH2)8CH3 | Pure | 20 | 68 |  |  |  | ++ | ++ | -- |  |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Dextrine (C6H10O5)n | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Diacetone alcohol (CH3)2C(OH)CH2COCH3 | Pure | 20 | 68 | -- | -- | ++ | ++ | ++ | ++ | -- |
|  |  | 40 | 104 |  |  | + | + | ++ |  |  |
|  |  | 60 | 140 |  |  |  | - | ++ |  |  |
|  |  | 80 | 176 |  |  |  | -- | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Dibenzyl ether (C6H5CH2)2O | Pure | 20 | 68 |  |  |  | ++ | ++ | - |  |
|  |  | 40 | 104 |  |  |  | + | ++ |  |  |
|  |  | 60 | 140 |  |  |  | - | ++ |  |  |
|  |  | 80 | 176 |  |  |  | -- | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Dibutyl amine (C4H9)2NH | Pure | 20 | 68 |  |  |  | ++ | ++ |  |  |
|  |  | 40 | 104 |  |  |  | - | ++ |  |  |
|  |  | 60 | 140 |  |  |  | -- | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Dibutyl ether [CH3(CH2)3]2O | Pure | 20 | 68 | -- | -- | - | ++ | ++ | -- | -- |
|  |  | 40 | 104 |  |  |  | + | ++ |  |  |
|  |  | 60 | 140 |  |  |  | - | ++ |  |  |
|  |  | 80 | 176 |  |  |  | -- | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Dibutyl phthalate C6H4(COOC4H9)2 | Pure | 20 | 68 | -- | -- |  | ++ | ++ | ++ | + |
|  |  | 40 | 104 |  |  |  | + | ++ | ++ |  |
|  |  | 60 | 140 |  |  |  | - | ++ |  |  |
|  |  | 80 | 176 |  |  |  | -- | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |

Chemical Resistance

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Dibutyl sebacate C4H9OCO(CH2)8COOC4H9 |  | 20 | 68 |  |  |  | ++ | ++ | + | - |
|  |  | 40 | 104 |  |  |  | + | ++ |  |  |
|  |  | 60 | 140 |  |  |  | - | ++ |  |  |
|  |  | 80 | 176 |  |  |  | -- | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Dichlorobenzene C6H4Cl2 | Pure | 20 | 68 | -- | -- |  | ++ | ++ | -- | + |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Dichloroethylene CH2=CCl2 | Pure | 20 | 68 | -- | -- |  | ++ | ++ | -- | + |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Dichloroisopropyl ether Cl-CH2-CH-O-CH-CH2-Cl CH3 CH3 | Pure | 20 | 68 |  |  |  | ++ | ++ |  |  |
|  |  | 40 | 104 |  |  |  | + | ++ |  |  |
|  |  | 60 | 140 |  |  |  | - | ++ |  |  |
|  |  | 80 | 176 |  |  |  | -- | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Diesel fuels |  | 20 | 68 |  |  |  | ++ | ++ |  |  |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Diethylamine (C2H5)2NH | Pure | 20 | 68 | -- | -- | ++ | + | ++ | ++ |  |
|  |  | 40 | 104 |  |  | + | - | ++ |  |  |
|  |  | 60 | 140 |  |  |  | -- | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Diethylene triamine NH(C2H4NH2)2 |  | 20 | 68 | -- | -- |  | ++ | ++ |  |  |
|  |  | 40 | 104 |  |  |  | + | ++ |  |  |
|  |  | 60 | 140 |  |  |  | - | ++ |  |  |
|  |  | 80 | 176 |  |  |  | -- | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Diethyl ether C2H5CO2H5 | Pure | 20 | 68 | -- | -- | - | ++ | ++ | -- | + |
|  |  | 40 | 104 |  |  | -- | + | ++ |  |  |
|  |  | 60 | 140 |  |  |  | - | ++ |  |  |
|  |  | 80 | 176 |  |  |  | -- |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Diglycolic acid O(CH2COOH)2 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Diisobutyl keton [(CH3)2CHCH2]2CO | Pure | 20 | 68 | -- | -- | ++ | ++ | ++ | -- | -- |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | + | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Diisobutylene C8H16 | Pure | 20 | 68 | -- | -- |  | ++ | ++ | -- | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  | ++ |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | + | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Diisopropyl keton [(CH3)2CH]2CO | Pure | 20 | 68 | -- | -- |  | -- | ++ | + | -- |
|  |  | 40 | 104 |  |  |  |  |  |  |  |
|  |  | 60 | 140 |  |  |  |  |  |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Dimethyl acetamide CH3CON(CH3)2 |  | 20 | 68 | -- | -- | -- | -- | ++ |  |  |
|  |  | 40 | 104 |  |  |  |  |  |  |  |
|  |  | 60 | 140 |  |  |  |  |  |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Dimethyl formamide HCON(CH3)2 | Pure | 20 | 68 | -- | -- | ++ | -- | ++ | ++ | -- |
|  |  | 40 | 104 |  |  | + |  | ++ |  |  |
|  |  | 60 | 140 |  |  |  |  | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Dimethyl phthalate C6H4(COOCH3)2 |  | 20 | 68 | -- | -- |  | + | ++ | + | + |
|  |  | 40 | 104 |  |  |  | - | ++ |  |  |
|  |  | 60 | 140 |  |  |  | -- |  |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Dimethyl sulfoxide (CH3)2SO |  | 20 | 68 |  |  |  | -- | ++ |  |  |
|  |  | 40 | 104 |  |  |  |  |  |  |  |
|  |  | 60 | 140 |  |  |  |  |  |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Dimethylamine (CH3)2NH | Pure | 20 | 68 | -- | -- | ++ | -- | ++ | - | -- |
|  |  | 40 | 104 |  |  | + |  | ++ | -- |  |
|  |  | 60 | 140 |  |  |  |  | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Dimethylaniline C8H11N | Pure | 20 | 68 | -- | -- |  | + | ++ | -- |  |
|  |  | 40 | 104 |  |  |  | - | ++ |  |  |
|  |  | 60 | 140 |  |  |  | -- | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Dioctyl phthalate C6H4(COOC8H17)2 |  | 20 | 68 | -- | -- |  | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 |  |  |  | + | ++ |  |  |
|  |  | 60 | 140 |  |  |  | - | ++ |  |  |
|  |  | 80 | 176 |  |  |  | -- | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Dioxane C4H8O2 | Pure | 20 | 68 | -- | -- | + | -- | ++ | - | -- |
|  |  | 40 | 104 |  |  | - |  |  |  |  |
|  |  | 60 | 140 |  |  |  |  |  |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Dioxolane OCH2CH2OCH2 |  | 20 | 68 | -- | -- |  | -- | ++ | -- | -- |
|  |  | 40 | 104 |  |  |  |  |  |  |  |
|  |  | 60 | 140 |  |  |  |  |  |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Diphenyl oxide C6H5OC6H5 | Satu | 20 | 68 | -- | -- |  |  | ++ |  | ++ |
|  |  | 40 | 104 |  |  |  |  |  |  |  |
|  |  | 60 | 140 |  |  |  |  |  |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Epichlorohydrin CH2-CH-CH2Cl O | Pure | 20 | 68 | -- | -- | -- | - | ++ | -- | -- |
|  |  | 40 | 104 |  |  |  | -- | ++ |  |  |
|  |  | 60 | 140 |  |  |  |  |  |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Ethanolamine H2NCH2CH2OH | Pure | 20 | 68 | -- | -- | ++ | -- | ++ | ++ | -- |
|  |  | 40 | 104 |  |  |  |  | ++ |  |  |
|  |  | 60 | 140 |  |  |  |  |  |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |

Chemical Resistance

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Ethyl acetate CH3COOC2H6 | Pure | 20 | 68 | -- | -- | + | + | ++ | + | -- |
|  |  | 40 | 104 |  |  | + | - | ++ |  |  |
|  |  | 60 | 140 |  |  | - |  | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Ethyl acetoacetate CH3COCH2COOC2H5 | Pure | 20 | 68 | -- | -- | -- | ++ | ++ | ++ | -- |
|  |  | 40 | 104 |  |  |  | + | ++ | ++ |  |
|  |  | 60 | 140 |  |  |  | - | ++ |  |  |
|  |  | 80 | 176 |  |  |  | -- | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Ethyl acrylate CH2CHCOOC2H5 | Pure | 20 | 68 | -- | -- |  | ++ | ++ | + | -- |
|  |  | 40 | 104 |  |  |  | + | ++ |  |  |
|  |  | 60 | 140 |  |  |  | - | ++ |  |  |
|  |  | 80 | 176 |  |  |  | -- | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Ethyl alcohol C2H5OH | Pure | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | + | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | + | + | + | ++ | ++ | ++ | + |
|  |  | 80 | 176 |  | - | + | ++ | ++ | ++ | + |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Ethyl benzene C6H5C2H5 |  | 20 | 68 | -- | -- |  | ++ | ++ | -- | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Ethyl chloride C2H5Cl |  | 20 | 68 | -- | -- | - | ++ | ++ | - | ++ |
|  |  | 40 | 104 |  |  | -- | ++ | ++ |  | ++ |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  | ++ |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  | + |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Ethyl ether (C2H5)2O | Pure | 20 | 68 | -- | -- | - | ++ | ++ | - | -- |
|  |  | 40 | 104 |  |  | -- | + | ++ |  |  |
|  |  | 60 | 140 |  |  |  | - | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Ethyl formate HCOOC2H5 | Pure | 20 | 68 |  |  |  | ++ | ++ | + | -- |
|  |  | 40 | 104 |  |  |  |  |  |  |  |
|  |  | 60 | 140 |  |  |  |  |  |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| 2-Ethyl hexanol C4H9CH(C2H5)CH2OH |  | 20 | 68 |  |  |  | ++ | ++ |  |  |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | + | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Ethyl Mercaptan C2H5SH | Pure | 20 | 68 |  |  |  | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 |  |  |  |  |  | ++ | ++ |
|  |  | 60 | 140 |  |  |  |  |  |  | ++ |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Ethyl Monochloroacetate ClCH2COO2H5 | Pure | 20 | 68 | - | -- | ++ | ++ | ++ | ++ | - |
|  |  | 40 | 104 |  |  | ++ | - | ++ |  |  |
|  |  | 60 | 140 |  |  | ++ |  | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| ethyl oxalate (COOC2H5)2 |  | 20 | 68 |  |  |  | -- | ++ | ++ | -- |
|  |  | 40 | 104 |  |  |  |  |  |  |  |
|  |  | 60 | 140 |  |  |  |  |  |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Ethylene chloride (Ethylene dichloride) |  | 20 | 68 | -- | -- | + | ++ | ++ | -- | ++ |
|  |  | 40 | 104 |  |  | -- | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Ethylene chlorohydrine ClCH2CH2OH | Pure | 20 | 68 | -- | -- | ++ | + | ++ | ++ | -- |
|  |  | 40 | 104 |  |  |  | - | ++ |  |  |
|  |  | 60 | 140 |  |  |  | -- | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Ethylene diamine NH2CH2CH2NH2 | Pure | 20 | 68 | -- | -- | + | + | ++ | ++ |  |
|  |  | 40 | 104 |  |  |  | -- | ++ |  |  |
|  |  | 60 | 140 |  |  |  |  | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Ethylene glycol CH2OHCH2OH | Pure | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | - |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ |  |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ |  |
|  |  | 80 | 176 |  | + | + | ++ | ++ | ++ |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ | + |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Ethylene glycol monoethyl ether C2H5O(CH2)2OH |  | 20 | 68 |  |  | ++ | ++ | ++ | - | + |
|  |  | 40 | 104 |  |  | ++ | + | ++ |  |  |
|  |  | 60 | 140 |  |  |  | - | ++ |  |  |
|  |  | 80 | 176 |  |  |  | -- | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Ethylene oxide ( CH2 )2O | Pure | 20 | 68 | -- | -- |  | + | ++ | -- | -- |
|  |  | 40 | 104 |  |  |  | - | ++ |  |  |
|  |  | 60 | 140 |  |  |  | -- | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Etnylene bromide CH2Br-CH2Br | Pure | 20 | 68 | -- | -- | -- | ++ | ++ | + | - |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Fatty acids RCOOH |  | 20 | 68 | ++ | + | ++ | ++ | ++ | -- | ++ |
|  |  | 40 | 104 | ++ | + | + | ++ | ++ |  |  |
|  |  | 60 | 140 | ++ | + | + | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  | - | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Ferric chloride FeCl3 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | + | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ | + | + |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Ferric hydroxide Fe(OH)3 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Ferric nitrate Fe(NO3)3 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | + | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Ferric sulfate Fe2(SO4)3 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |

Chemical Resistance

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Ferrous acetate Fe(CH3COO)2 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | + | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | + | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | + |  |  |  |
| Ferrous chloride FeCl2 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ | + | + |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Ferrous hydroxide Fe(OH)2 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Ferrous nitrate Fe(NO3)2 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Ferrous sulfate FeSO4 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ | + | + |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Fluoboric acid HBF4 | Pure | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | + | ++ | ++ | ++ | ++ | ++ | + |
|  |  | 80 | 176 |  | + | + | ++ | ++ | + | -- |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Fluorine gas F2 | Wet | 20 | 68 | -- | -- | -- | -- | ++ | -- | - |
|  |  | 40 | 104 |  |  |  |  | ++ |  |  |
|  |  | 60 | 140 |  |  |  |  | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Fluosilicic acid H2SiF6 | 50 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | + | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | + | ++ | ++ | + | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ | + | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Formaldehyde HCHO | 35 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | - | + | ++ | + | ++ | + | + |
|  |  | 80 | 176 |  |  | + | -- | ++ | + | - |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Formic acid HCOOH | 90 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | - |
|  |  | 40 | 104 | + | + | + | ++ | ++ | ++ |  |
|  |  | 60 | 140 | -- | -- | -- | ++ | ++ | ++ |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ | ++ |  |
|  |  | 100 | 212 |  |  |  | + | ++ | + |  |
|  |  | 120 | 248 |  |  |  | - | ++ |  |  |
| Freon-11 CCl3F |  | 20 | 68 | - | ++ | -- | ++ | ++ | -- | + |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Freon-113 CCl2F-CClF2 |  | 20 | 68 | + | ++ | ++ | ++ | ++ | - | + |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Freon-114 CClF2-CClF2 |  | 20 | 68 | + |  |  | ++ | ++ | - | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  | ++ |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Freon-12 CCl2F2 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | - | - |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Freon-21 CHCl2F |  | 20 | 68 | -- | + | + | ++ | ++ | -- | -- |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Freon-22 CHClF2 |  | 20 | 68 | -- | - | + | ++ | ++ | + | -- |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Fructose (Fruits sugar) |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  |  | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Fuming sulfuric acid H2SO4+SO3 |  | 20 | 68 | -- | -- | -- | -- | ++ | -- | - |
|  |  | 40 | 104 |  |  |  |  |  |  |  |
|  |  | 60 | 140 |  |  |  |  |  |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Furan | C C | O | C C |  | 20 | 68 |  |  |  | -- | ++ | -- | -- |
|  |  |  |  |  | 40 | 104 |  |  |  |  |  |  |  |
|  |  |  |  |  | 60 | 140 |  |  |  |  |  |  |  |
|  |  |  |  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  |  |  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  |  |  |  | 120 | 248 |  |  |  |  |  |  |  |
| Furfural C4H3OCHO | Pure | 20 | 68 | -- | -- | ++ | + | ++ | ++ | -- |
|  |  | 40 | 104 |  |  |  | - | ++ | ++ |  |
|  |  | 60 | 140 |  |  |  | -- | ++ | + |  |
|  |  | 80 | 176 |  |  |  |  | ++ | - |  |
|  |  | 100 | 212 |  |  |  |  | ++ | -- |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Furfuril alcohol C4H3OCH2OH | Pure | 20 | 68 | -- | -- |  | + | ++ | - | -- |
|  |  | 40 | 104 |  |  |  | + | ++ |  |  |
|  |  | 60 | 140 |  |  |  | - | ++ |  |  |
|  |  | 80 | 176 |  |  |  | -- |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Furric sulfide Fe2S3 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | + | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Gallic acid C6H2(OH)3COOH |  | 20 | 68 |  |  |  | + | ++ | ++ | ++ |
|  |  | 40 | 104 |  |  |  | + | ++ |  |  |
|  |  | 60 | 140 |  |  |  | - | ++ |  |  |
|  |  | 80 | 176 |  |  |  | -- | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Gasoline |  | 20 | 68 | + |  | -- | ++ | ++ | -- | + |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |

Chemical Resistance

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Gelatine |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Glacial acetic acid CH3COOH |  | 20 | 68 | -- | -- | + | ++ | ++ | - | -- |
|  |  | 40 | 104 |  |  | - | ++ | ++ | -- |  |
|  |  | 60 | 140 |  |  | -- | + | ++ |  |  |
|  |  | 80 | 176 |  |  |  | + | ++ |  |  |
|  |  | 100 | 212 |  |  |  | - | ++ |  |  |
|  |  | 120 | 248 |  |  |  | -- | ++ |  |  |
| Glucose C6H12O6 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Glycerol(Glycerine) C3H5(OH)3 | Pure | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Glycolic acid CH2(OH)COOH | Satu | 20 | 68 |  |  | ++ | + | ++ | ++ | ++ |
|  |  | 40 | 104 |  |  | ++ | - | ++ |  |  |
|  |  | 60 | 140 |  |  | ++ | -- | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Grape suger C6H12O6 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Heavy oil |  | 20 | 68 | - | -- | -- | ++ | ++ | -- | -- |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Heptane CH3(CH2)5CH3 |  | 20 | 68 | ++ |  | + | ++ | ++ | -- | ++ |
|  |  | 40 | 104 | ++ |  | + | ++ | ++ |  | ++ |
|  |  | 60 | 140 | ++ |  | - | ++ | ++ |  | ++ |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Hexane C6H14 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | -- | ++ |
|  |  | 40 | 104 | + |  | + | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  | - | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Hexyl alcohol CH3(CH2)5OH | Pure | 20 | 68 | ++ | ++ | ++ | ++ | ++ | + | ++ |
|  |  | 40 | 104 | ++ |  |  | ++ | ++ | + | ++ |
|  |  | 60 | 140 | + |  |  | ++ | ++ | - | ++ |
|  |  | 80 | 176 |  |  |  | + | ++ | -- | ++ |
|  |  | 100 | 212 |  |  |  |  | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  |  | ++ |  | + |
| Hydeogen peroxide H2O2 | 5 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | + | ++ |
|  |  | 60 | 140 | - | - | ++ | ++ | ++ | + | ++ |
|  |  | 80 | 176 |  | - | + | ++ | ++ | - | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Hydrazine H2NNH2 | Pure | 20 | 68 | -- | -- | - | - | ++ | ++ | -- |
|  |  | 40 | 104 |  |  | -- | - | ++ |  |  |
|  |  | 60 | 140 |  |  |  | -- | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Hydrobromic acid HBr |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | + | ++ | ++ | ++ | ++ | + | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | - | + |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | + | ++ |  |  |
| Hydrochloric acid HCl | 15 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | + | + |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | - | - |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | -- | -- |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Hydrochloric acid HCl | 25 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | + | + |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | - | - |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | -- | -- |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | + | ++ |  |  |
| Hydrochloric acid HCl | 35 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | + | + |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | + | - |
|  |  | 60 | 140 | + | ++ | ++ | ++ | ++ | -- | -- |
|  |  | 80 | 176 |  | + | + | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | + | ++ |  |  |
|  |  | 120 | 248 |  |  |  | - | ++ |  |  |
| Hydrochloric acid HCl | 38 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | + | + |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | - | - |
|  |  | 60 | 140 | + | + | ++ | ++ | ++ | -- | -- |
|  |  | 80 | 176 |  | + | + | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | + | ++ |  |  |
|  |  | 120 | 248 |  |  |  | - | ++ |  |  |
| Hydrocyanic acid HCN | 10 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | + | + |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ |  |  |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Hydrofluoric acid HF | Dilute | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | + | + | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | - | + | + | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | - | + | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  | + | ++ | ++ | ++ | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  | + |
| Hydrofluoric acid HF | 30 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | + | + | + | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | - | - | + | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 | -- | -- | + | ++ | ++ | + | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ | -- | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Hydrofluoric acid HF | 40 | 20 | 68 | + | + | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | - | - | + | ++ | ++ | + | ++ |
|  |  | 60 | 140 | -- | -- | + | ++ | ++ | - | ++ |
|  |  | 80 | 176 |  |  | + | ++ | ++ | -- | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | + |
|  |  | 120 | 248 |  |  |  | + | ++ |  |  |
| Hydrofluoric acid HF | 50 | 20 | 68 | + | + | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | - | -- | + | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | -- |  | + | ++ | ++ | + | ++ |
|  |  | 80 | 176 |  |  | + | ++ | ++ | - | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ | -- | + |
|  |  | 120 | 248 |  |  |  | + | ++ |  | - |
| Hydrogen H2 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Hydrogen fluoride HF |  | 20 | 68 |  |  |  | ++ | ++ | + | -- |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |

Chemical Resistance

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Hydrogen peroxide H2O2 | 20 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | + | ++ | ++ | ++ | + | ++ |
|  |  | 60 | 140 | - | - | ++ | ++ | ++ | + | ++ |
|  |  | 80 | 176 |  | - | + | ++ | ++ | - | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Hydrogen peroxide H2O2 | 30 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | + | - | + | ++ | ++ | - | + |
|  |  | 60 | 140 | + |  | + | ++ | ++ | -- | - |
|  |  | 80 | 176 |  |  | - | ++ | ++ |  | - |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Hydrogen peroxide H2O2 | 50 | 20 | 68 | + | - | - | ++ | ++ | -- | - |
|  |  | 40 | 104 | - | -- | -- | ++ | ++ |  | -- |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | + | ++ |  |  |
| Hydrogen peroxide H2O2 | 90 | 20 | 68 | + | -- | -- | ++ | ++ | -- | -- |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Hydrogen sulfide H2S |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | + |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ | + |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Hydrogen sulfide H2S | Gas | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | + |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ |  |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ |  |
|  |  | 80 | 176 |  | + | ++ | ++ | ++ | + |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ | + |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Hydroiodic acid HI |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Hydroquinone C6H4(OH)2 | Satu | 20 | 68 | ++ |  |  | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ |  |  | ++ | ++ |  | ++ |
|  |  | 60 | 140 | ++ |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Hypochlorous acid HClO | 10 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | + | ++ | ++ | + | + |
|  |  | 60 | 140 | -- | ++ | + | ++ | ++ |  |  |
|  |  | 80 | 176 |  | + |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | + | ++ |  |  |
| Iodine I2 |  | 20 | 68 | + | + | ++ | ++ | ++ | -- | + |
|  |  | 40 | 104 | - | + | ++ | ++ | ++ |  |  |
|  |  | 60 | 140 |  | - | ++ | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  | ++ | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Iodine solutions | 10 | 20 | 68 | ++ |  |  | ++ | ++ |  |  |
|  |  | 40 | 104 | ++ |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Isobutyl alcohol (CH3)2CHCH2OH | Pure | 20 | 68 |  |  |  | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Iso-octane (CH3)3CCH2 |  | 20 | 68 | ++ | + | ++ | ++ | ++ | -- | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Isophrone C9H14O | Pure | 20 | 68 | -- | -- |  |  | ++ | -- | -- |
|  |  | 40 | 104 |  |  |  |  |  |  |  |
|  |  | 60 | 140 |  |  |  |  |  |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Isopropyl acetate CH3COOCH(CH3)2 | Pure | 20 | 68 |  |  |  |  | ++ | + | -- |
|  |  | 40 | 104 |  |  |  |  | ++ |  |  |
|  |  | 60 | 140 |  |  |  |  | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Isopropyl alcohol (CH3)2CHOH | Pure | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  | ++ |
|  |  | 100 | 212 |  |  |  |  | ++ |  | + |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Isopropyl chloride ( CH3 ) 2CHCl |  | 20 | 68 |  |  |  | ++ | ++ | -- | ++ |
|  |  | 40 | 104 |  |  |  | + | ++ |  |  |
|  |  | 60 | 140 |  |  |  | - | ++ |  |  |
|  |  | 80 | 176 |  |  |  | -- | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Isopropyl ether (CH3)2CH-O-CH(CH3)2 | Pure | 20 | 68 |  |  |  | ++ | ++ | - | - |
|  |  | 40 | 104 |  |  |  | + | ++ |  |  |
|  |  | 60 | 140 |  |  |  | - | ++ |  |  |
|  |  | 80 | 176 |  |  |  | -- | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Jet fuel Jp-4 |  | 20 | 68 |  |  |  | ++ | ++ | -- | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Jet fuel Jp-5 |  | 20 | 68 |  |  |  | ++ | ++ | -- | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Kerosene(kerosine) |  | 20 | 68 | + | + | ++ | ++ | ++ | -- | ++ |
|  |  | 40 | 104 | + | + | + | ++ | ++ |  |  |
|  |  | 60 | 140 | - | - | - | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | + | ++ |  |  |
| Lactic acid CH3CH(OH)COOH | 25 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | + | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ | ++ | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Lactic acid CH3CH(OH)COOH | 80 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | + | ++ | ++ | + | ++ | ++ | ++ |
|  |  | 60 | 140 | + | + | ++ | - | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  | + | - | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | -- | ++ | + | + |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Laquer |  | 20 | 68 | -- | -- | ++ | ++ | ++ | -- | -- |
|  |  | 40 | 104 |  |  |  |  |  |  |  |
|  |  | 60 | 140 |  |  |  |  |  |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |

Chemical Resistance

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Lauric acid CH3(CH2)10COOH |  | 20 | 68 |  |  |  | ++ | ++ |  |  |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Lauroyl chloride C11H23COCl | Pure | 20 | 68 |  |  |  | ++ | ++ |  |  |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Lead acetate Pb(CH3COO)2 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | + |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | + |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Lead chloride PbCl2 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  |  | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Lead nitrate Pb(NO3)2 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Lead sulfate PbSO4 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Lemon oil |  | 20 | 68 |  |  | -- | ++ | ++ |  |  |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Linolenic acid C17H29COOH |  | 20 | 68 | + | + | + | ++ | ++ | -- | ++ |
|  |  | 40 | 104 | + | + |  | ++ | ++ |  |  |
|  |  | 60 | 140 | + | + |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Linolenic oil C17H31COOH |  | 20 | 68 | + | + |  | ++ | ++ |  |  |
|  |  | 40 | 104 | + | + |  | ++ | ++ |  |  |
|  |  | 60 | 140 | + | + |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Linseed oil |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | -- | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ |  | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ |  | ++ |
|  |  | 80 | 176 |  | ++ | + | ++ | ++ |  | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Lithium bromide LiBr | 60 | 20 | 68 | ++ |  | ++ | ++ | ++ |  | ++ |
|  |  | 40 | 104 | ++ |  |  | ++ | ++ |  | ++ |
|  |  | 60 | 140 | ++ |  |  | ++ | ++ |  | ++ |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Lithium chloride LiCl | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ |  | ++ |
|  |  | 80 | 176 |  |  | ++ | ++ | ++ |  | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | + |  |  |  |

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Lithium hydroxide LiOH |  | 20 | 68 | ++ |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  | ++ | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Lubricating oil(ASTM1) |  | 20 | 68 | ++ | ++ | + | ++ | ++ | -- | ++ |
|  |  | 40 | 104 | + |  | + | ++ | ++ |  | ++ |
|  |  | 60 | 140 | - |  | - | ++ | ++ |  | ++ |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | + |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Lubricating oil(ASTM2) |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | -- | ++ |
|  |  | 40 | 104 | + |  | + | ++ | ++ |  | ++ |
|  |  | 60 | 140 | - |  | - | ++ | ++ |  | ++ |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | + |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Lubricating oil(ASTM3) |  | 20 | 68 | ++ | ++ | - | ++ | ++ | -- | ++ |
|  |  | 40 | 104 | + |  | -- | ++ | ++ |  | ++ |
|  |  | 60 | 140 | - |  |  | ++ | ++ |  | ++ |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  | + |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | + |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Magnesium hydroxide | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | + | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | + | ++ |  |  |
| Magnesium carbonate |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Magnesium chloride MgCl2 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | + | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ | + | + |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Magnesium citrate Mg3(C6H5O7)2 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Magnesium notrate Mg(NO3)2 · 6H2O |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | + | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Maleic acid (CHCOOH)2 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | + | ++ |
|  |  | 60 | 140 | + | ++ | ++ | ++ | ++ | + | + |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ |  | + |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Malic acid HOOCCH2CH(OH)COOH | 10 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | + |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ | + |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Manganese chloride MnCl2 |  | 20 | 68 | ++ |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | + |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  | ++ | ++ | ++ |  | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |

Chemical Resistance

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Manganese sulfate MnSO4 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Mercuric chloride HgCl2 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  | ++ | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Mercuric cyanide Hg(CN)2 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ |  | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ |  | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Mercuric sulfate HgSO4 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Mercurous nitrate Hg2(NO3)2 | Satu | 20 | 68 | ++ |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Mercury Hg |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ |  |  |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ |  |  |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Methane CH4 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | + | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | + | + | + | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | + | ++ | ++ | + | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ | - | + |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Methanesulfonic acid CH3SO3H | Pure | 20 | 68 |  |  |  | ++ | ++ |  |  |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Methyl acetate CH3COOCH3 | Pure | 20 | 68 | -- | -- | + | ++ | ++ | + | -- |
|  |  | 40 | 104 |  |  |  | + | ++ | - |  |
|  |  | 60 | 140 |  |  |  | - | ++ |  |  |
|  |  | 80 | 176 |  |  |  | -- | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Methyl acrylate CH2CHCOOCH3 | Pure | 20 | 68 |  |  |  | ++ | ++ | + | -- |
|  |  | 40 | 104 |  |  |  | + | ++ |  |  |
|  |  | 60 | 140 |  |  |  | - | ++ |  |  |
|  |  | 80 | 176 |  |  |  | -- | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Methyl alcohol CH3OH | Pure | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | -- |
|  |  | 40 | 104 | + | + | ++ | ++ | ++ | ++ |  |
|  |  | 60 | 140 | + | + | ++ | ++ | ++ | ++ |  |
|  |  | 80 | 176 |  |  | + | ++ | ++ | + |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Methyl amine CH3NH2 |  | 20 | 68 | -- | -- | -- | - | ++ | ++ |  |
|  |  | 40 | 104 |  |  |  | -- | ++ |  |  |
|  |  | 60 | 140 |  |  |  |  | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Methyl bromide CH3Br |  | 20 | 68 | -- | -- | -- | ++ | ++ | -- | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Methyl cellosolve HOCH2CH2OCH3 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | + |  |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Methyl chloride CH3Cl |  | 20 | 68 | -- | -- | - | ++ | ++ | + | -- |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Methyl chloroform CH3CCl3 |  | 20 | 68 | -- | -- | - | ++ | ++ | -- | + |
|  |  | 40 | 104 |  |  |  | + | ++ |  |  |
|  |  | 60 | 140 |  |  |  | - | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Methyl ether (CH3)2O |  | 20 | 68 |  |  |  | ++ | ++ | -- | -- |
|  |  | 40 | 104 |  |  |  |  |  |  |  |
|  |  | 60 | 140 |  |  |  |  |  |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Methyl ethyl ketone CH3COC2H5 |  | 20 | 68 | -- | -- | + | - | ++ | + | -- |
|  |  | 40 | 104 |  |  | - | -- | ++ | - |  |
|  |  | 60 | 140 |  |  | -- |  | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | + |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Methyl formate HCOOCH3 |  | 20 | 68 |  |  |  | ++ | ++ | ++ | -- |
|  |  | 40 | 104 |  |  |  | + | ++ |  |  |
|  |  | 60 | 140 |  |  |  | - | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Methyl isobutyl carbinol C4H9CH(CH3)OH |  | 20 | 68 |  |  |  |  | ++ | ++ | ++ |
|  |  | 40 | 104 |  |  |  |  | ++ |  |  |
|  |  | 60 | 140 |  |  |  |  | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Methyl isobutyl ketone (CH3)2CHCH2COCH3 |  | 20 | 68 | -- | -- | + | - | ++ | + | -- |
|  |  | 40 | 104 |  |  | -- | -- | ++ |  |  |
|  |  | 60 | 140 |  |  |  |  | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Methyl isopropyl ketone CH3COCH(CH3)2 |  | 20 | 68 | -- | -- |  | -- | ++ | -- |  |
|  |  | 40 | 104 |  |  |  |  | ++ |  |  |
|  |  | 60 | 140 |  |  |  |  | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Methyl methacrylate CH2C(CH3)COOCH3 |  | 20 | 68 |  |  |  | ++ | ++ | -- | -- |
|  |  | 40 | 104 |  |  |  | + | ++ |  |  |
|  |  | 60 | 140 |  |  |  | - | ++ |  |  |
|  |  | 80 | 176 |  |  |  | -- | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Methyl salicylate C6H4(OH)COOCH3 |  | 20 | 68 |  |  | ++ | ++ | ++ | -- | ++ |
|  |  | 40 | 104 |  |  |  |  |  |  |  |
|  |  | 60 | 140 |  |  |  |  |  |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |

Chemical Resistance

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Methylaniline C6H5NHCH3 |  | 20 | 68 |  |  |  | ++ | ++ | -- | ++ |
|  |  | 40 | 104 |  |  |  | + | ++ |  |  |
|  |  | 60 | 140 |  |  |  | -- | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Methylene bromide CH2Br2 |  | 20 | 68 |  |  |  | ++ | ++ | -- | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 |  |  |  |  |  | ++ |  |  |
| Methylene chloride CH2Cl2 |  | 20 | 68 | -- | -- | -- | + | ++ | -- | - |
|  |  | 40 | 104 |  |  |  | - | ++ |  |  |
|  |  | 60 | 140 |  |  |  | -- | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Methylene iodide CH2I2 |  | 20 | 68 |  |  |  | ++ | ++ |  | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  | ++ |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  | ++ |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  | ++ |
|  |  | 100 | 212 |  |  |  |  | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Mgnesium sulfate MgSO4 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ | + | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Morpholine CH2CH2 O NH CH2CH2 | Pure | 20 | 68 | -- | -- | ++ | ++ | ++ | - | ++ |
|  |  | 40 | 104 |  |  | ++ | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  | ++ | - | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Naphthalene C10H8 |  | 20 | 68 | -- | -- | + | ++ | ++ | -- | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Natural gas |  | 20 | 68 | ++ |  |  | ++ | ++ | -- | ++ |
|  |  | 40 | 104 | ++ |  |  | ++ | ++ |  | ++ |
|  |  | 60 | 140 | + |  |  | ++ | ++ |  | ++ |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  | + |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Nickel acetate Ni(CH3COO)2 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | - |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ |  |  |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ |  |  |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Nickel aminosulfonate Ni(NH2SO3)2 · H2O |  | 20 | 68 |  |  |  | ++ | ++ | ++ |  |
|  |  | 40 | 104 |  |  |  | ++ | ++ | ++ |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ | ++ |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Nickel chloride NiCl2 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ | + | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Nickel nitrate Ni(NO3)2 · 6H2O | Satu | 20 | 68 | ++ |  |  | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 |  |  |  | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  |  | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ | ++ | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  | ++ |

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Nickel sulfate NiSO4 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | + | ++ | ++ | ++ | + |
|  |  | 100 | 212 |  |  |  | ++ | ++ | + |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Nicotine C10H14N2 |  | 20 | 68 |  |  |  | ++ | ++ |  |  |
|  |  | 40 | 104 |  |  |  | + | ++ |  |  |
|  |  | 60 | 140 |  |  |  |  | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Nicotinic acid C5H4NCOOH |  | 20 | 68 |  |  |  | ++ | ++ | ++ |  |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Nitric acid HNO3 | 10 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | - | ++ | ++ | ++ | ++ | + | + |
|  |  | 80 | 176 |  | + | + | ++ | ++ | -- | -- |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Nitric acid HNO3 | 30 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | + | ++ |
|  |  | 40 | 104 | + | + | ++ | ++ | ++ | + | ++ |
|  |  | 60 | 140 | - | - | + | ++ | ++ | -- | + |
|  |  | 80 | 176 |  | -- | + | ++ | ++ |  | - |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | - |
|  |  | 120 | 248 |  |  |  | + | ++ |  |  |
| Nitric acid HNO3 | 50 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | -- | ++ |
|  |  | 40 | 104 | + | + | + | ++ | ++ |  | + |
|  |  | 60 | 140 | - | -- | - | + | ++ |  | - |
|  |  | 80 | 176 |  |  | -- | + | ++ |  | -- |
|  |  | 100 | 212 |  |  |  | - | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Nitric acid HNO3 | 70 | 20 | 68 | ++ | + | - | ++ | ++ | -- | -- |
|  |  | 40 | 104 | + | -- | -- | ++ | ++ |  |  |
|  |  | 60 | 140 | - |  |  | + | ++ |  |  |
|  |  | 80 | 176 |  |  |  | - | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Nitric acid HNO3 | 98 | 20 | 68 | -- | -- | -- | - | ++ | -- | -- |
|  |  | 40 | 104 |  |  |  | -- | + |  |  |
|  |  | 60 | 140 |  |  |  |  | + |  |  |
|  |  | 80 | 176 |  |  |  |  | - |  |  |
|  |  | 100 | 212 |  |  |  |  | - |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Nitrobenzene C6H5NO2 |  | 20 | 68 | -- | -- | + | ++ | ++ | ++ | -- |
|  |  | 40 | 104 |  |  | - | + | ++ |  |  |
|  |  | 60 | 140 |  |  | - | - | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Nitroethane CH3CH2NO2 | Pure | 20 | 68 |  |  |  | ++ | ++ | ++ | -- |
|  |  | 40 | 104 |  |  |  |  | ++ |  |  |
|  |  | 60 | 140 |  |  |  |  | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Nitrogen dioxide NO2 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 |  |  |  | + | ++ |  |  |
|  |  | 60 | 140 |  |  |  | + | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Nitrogen monoxide NO |  | 20 | 68 | ++ |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |

Chemical Resistance

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Nitromethane CH3NO2 | Pure | 20 | 68 |  |  |  | ++ | ++ | + | -- |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  |  | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Nitrotoluene NO2C6H4CH3 | Pure | 20 | 68 | -- | -- | ++ | ++ | ++ | -- | - |
|  |  | 40 | 104 |  |  | ++ | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Nitrous acid HNO2 | 10 | 20 | 68 |  |  |  | ++ | ++ | + | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Nitrous oxide N2O |  | 20 | 68 | ++ |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  | ++ | ++ | ++ | + | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | + |
|  |  | 120 | 248 |  |  |  | + | ++ |  | + |
| Octane C8H18 |  | 20 | 68 |  |  |  | ++ | ++ | -- | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Octene CH3(CH2)5CH=CH2 | Pure | 20 | 68 |  |  |  | ++ | ++ | -- | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Oleic acid C8H17CH=CH(CH2)7COOH |  | 20 | 68 | ++ | + | ++ | ++ | ++ | -- | ++ |
|  |  | 40 | 104 | ++ | + | ++ | ++ | ++ |  | ++ |
|  |  | 60 | 140 | + | + | ++ | ++ | ++ |  | ++ |
|  |  | 80 | 176 |  |  | ++ | ++ | ++ |  | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | + | ++ |  | + |
| Olive oil |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | + | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ |  | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ |  | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Oxalic acid HOOCCOOH | 20 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | + |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ |  |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ |  |  |
|  |  | 80 | 176 |  | ++ | ++ | + | ++ |  |  |
|  |  | 100 | 212 |  |  |  | - | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Oxalic acid HOOCCOOH | 50 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | + |
|  |  | 40 | 104 | ++ | ++ | ++ | + | ++ | ++ |  |
|  |  | 60 | 140 | ++ | ++ | ++ | - | ++ |  |  |
|  |  | 80 | 176 |  | ++ | ++ | - | ++ |  |  |
|  |  | 100 | 212 |  |  |  | -- | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Oxygen gas O2 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Ozone O3 |  | 20 | 68 | + | + | -- | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | + | + |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Palmitic acid C15H31COOH | Pure | 20 | 68 | ++ |  | ++ | ++ | ++ | + | ++ |
|  |  | 40 | 104 |  |  | ++ | ++ | ++ | - |  |
|  |  | 60 | 140 |  |  | ++ | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  | + | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Paraffin |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | -- | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ |  | ++ |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  | ++ |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Peanut oil |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ |  |  |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Perchloric acid HClO4 | 10 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | + | ++ |
|  |  | 40 | 104 | - | + | + | ++ | ++ |  |  |
|  |  | 60 | 140 | -- | - |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  | -- |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Perchloric acid HClO4 | 70 | 20 | 68 |  |  |  | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  |  | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Perphosphate |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ |  |  |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ |  |  |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Petroleum oil |  | 20 | 68 | + | + | + | ++ | ++ | -- | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Phenol C6H5OH | Pure | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | - |
|  |  | 40 | 104 |  |  | ++ | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  | + | + | ++ |  |  |
|  |  | 80 | 176 |  |  | -- | - | ++ |  |  |
|  |  | 100 | 212 |  |  |  | - | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Phenyl disulfide C6H5SSC6H5 |  | 20 | 68 |  |  |  |  | ++ | -- | ++ |
|  |  | 40 | 104 |  |  |  |  | ++ |  |  |
|  |  | 60 | 140 |  |  |  |  | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Phenylhydrazine C6H5NHNH2 |  | 20 | 68 | -- | -- | -- | ++ | ++ | + | -- |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | + |  |  |  |
|  |  | 80 | 176 |  |  |  | + |  |  |  |
|  |  | 100 | 212 |  |  |  | - |  |  |  |
|  |  | 120 | 248 |  |  |  | -- |  |  |  |
| Phosgene gas COCl2 |  | 20 | 68 | -- | -- | -- |  |  |  | -- |
|  |  | 40 | 104 |  |  |  |  |  |  |  |
|  |  | 60 | 140 |  |  |  |  |  |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Phosphoric acid H3PO4 | 10 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ | ++ |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Phosphoric acid H3PO4 | 50 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | + | + | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | -- | - | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | -- | - | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ | ++ |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Phosphoric acid H3PO4 | 80 | 20 | 68 | + | + | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | - | + | + | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | -- | - | + | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | -- | - | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ | ++ |  |
|  |  | 120 | 248 |  |  |  | + | ++ |  |  |
| Phosphorus pentoxide P2O5 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Phosphorus red P4 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ |  |  |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Phosphorus trichloride PCl3 | Pure | 20 | 68 | -- | -- | -- | ++ | ++ | -- | - |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  | -- |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Phosphrus oxychloride POCl3 |  | 20 | 68 | -- | -- | -- | -- | + | -- | -- |
|  |  | 40 | 104 |  |  |  |  | - |  |  |
|  |  | 60 | 140 |  |  |  |  |  |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Phtharic acid C6H4(COOH)2 |  | 20 | 68 | -- | -- | -- | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | + | ++ |  |  |
|  |  | 100 | 212 |  |  |  | + | ++ |  |  |
|  |  | 120 | 248 |  |  |  | - | ++ |  |  |
| Picric acid C6H2(OH)(NO2)3 | 10 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | ++ | ++ | ++ | + | + |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | - |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Poly aluminium chloride [Al2(OH)nCl6-n]m |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Polyethylene glycol H(OCH2CH2)nOH |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | + | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Polyvinyl acetate [CH2CH(OCOCH3)]n |  | 20 | 68 |  |  |  | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Polyvinyl alcohol [-CH2-CH(OH)-]n |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ |  | ++ |
|  |  | 80 | 176 |  |  | ++ | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Potassium hypochlorite |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Potassium permanganate KMnO4 | 10 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | + | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | + | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Potassium permanganate KMnO4 | 25 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | + |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | + |
|  |  | 60 | 140 | + | ++ | ++ | ++ | ++ | ++ |  |
|  |  | 80 | 176 |  | + | + | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Potassium acetate CH3COOK | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Potassium aluminium silicate Al2O3 · K2O · 6SiO2 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Potassium bichromate K2Cr2O7 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | + | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | - | - | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | -- | + | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Potassium bisulfate(Potassium hydrogen sulfate) KHSO4 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Potassium borate K2B4O7 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Potassium bromate KBrO3 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | + | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Potassium bromide KBr |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Potassium carbonate K2CO3 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Potassium chlorate KClO3 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | + | ++ | ++ | ++ | ++ |  | ++ |
|  |  | 80 | 176 |  | + | + | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |

Chemical Resistance

Chemical Resistance

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Potassium chloride KCl |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Potassium chromate K2CrO4 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | + | + | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | + | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | + | ++ |  |  |
| Potassium coppercyanide K3[Cu(CN4)] |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  | + | ++ | ++ | + | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Potassium cyanide KCN |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | + | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | + |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Potassium ferricyanide K3[Fe(CN)6] |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Potassium ferrocyanide K4[Fe(CN)6] |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Potassium fluoride KF |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 |  |  |  | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  |  | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Potassium hydrogen carbonate KHCO3 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Potassium hydroxide KOH |  | 20 | 68 |  |  |  |  |  |  |  |
|  |  | 40 | 104 |  |  |  |  |  |  |  |
|  |  | 60 | 140 |  | Refer to page99 (Caustic potash) |  |
|  |  | 80 | 176 |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Potassium iodide KI |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Potassium nitrate KNO3 |  | 20 | 68 | ++ | ++ |  | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ |  | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ |  | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  |  | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Potassium perborate KBO3 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ |  |  |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ |  |  |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ |  |  |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Potassium perchlorate KCl4 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ |  |  |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ |  |  |
|  |  | 60 | 140 | ++ | ++ | + | ++ | ++ |  |  |
|  |  | 80 | 176 |  | + |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ |  |  |  |
|  |  | 120 | 248 |  |  |  | ++ |  |  |  |
| Potassium persulfate K2S2O8 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ |  |  |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Potassium phosphate K3PO4 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | - |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Potassium sulfate K2SO4 | Pure | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | + | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Potassium sulfite K2SO3 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Potassium thiocyanate KSCN |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | - | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ |  | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ |  | ++ |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | + | ++ |  |  |
| Propane CH3CH2CH3 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | -- | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Propionic acid CH3CH2COOH | 50 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | - | + |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ |  |  |
|  |  | 60 | 140 |  | ++ | ++ | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| propyl acetate CH3COOC3H7 | Pure | 20 | 68 |  |  |  | ++ | ++ | + | -- |
|  |  | 40 | 104 |  |  |  | + | ++ |  |  |
|  |  | 60 | 140 |  |  |  | - | ++ |  |  |
|  |  | 80 | 176 |  |  |  | -- |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Propyl alcohol C3H7OH | Pure | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | + | ++ | ++ | + | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | + | + | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | - | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Propylene dichloride CH3CHClCH2Cl | pure | 20 | 68 | -- | -- | -- | ++ | ++ | -- | + |
|  |  | 40 | 104 |  |  |  |  |  |  |  |
|  |  | 60 | 140 |  |  |  |  |  |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Propylene oxide C3H6O |  | 20 | 68 | -- | -- | + | -- | ++ | - | -- |
|  |  | 40 | 104 |  |  |  |  |  |  |  |
|  |  | 60 | 140 |  |  |  |  |  |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Pyridine C5H5N |  | 20 | 68 | -- | -- | ++ | - | ++ | + | -- |
|  |  | 40 | 104 |  |  | ++ | - | ++ | - |  |
|  |  | 60 | 140 |  |  | + | -- | ++ | -- |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Salicyl aldehyde C6H4(OH)(CHO) |  | 20 | 68 |  |  |  | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 |  |  |  | + | ++ |  |  |
|  |  | 60 | 140 |  |  |  | - | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Salicylic acid C6H4(OH)(COOH) |  | 20 | 68 | ++ |  |  | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | + | ++ |  |  |
|  |  | 120 | 248 |  |  |  | - | ++ |  |  |
| Silicic acid SiO3 · nH2O |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Silicon oil |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ |  | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  | ++ | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Silver chloride AgCl |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Silver cyanide AgCN |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Silver nitrate AgNO3 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Silver sulfate Ag2SO4 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Soaps |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Sodium bisulfite NaHSO3 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | + | ++ | ++ | + | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Sodium acetate CH3COONa | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | + |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | - |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | - |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Sodium Ammonium sulfate NaAl(SO4)2 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | + |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ |  |  |  |
| Sodium benzoate C6H5COONa |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ |  |  |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ |  |  |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  | ++ | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Sodium bichromate Na2Cr2O7 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | + | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | - | - | + | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | -- | + | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Sodium bromide NaBr | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ |  |  |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Sodium carbonate Na2CO3 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Sodium chlorate NaClO3 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | + | + | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | + | ++ | ++ | ++ | + |
|  |  | 100 | 212 |  |  |  | ++ | ++ | + | + |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Sodium chloride NaCl |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Sodium chlorite NaClO2 | 25 | 20 | 68 | -- | -- |  | ++ | ++ | + | + |
|  |  | 40 | 104 |  |  |  | + | + | + | + |
|  |  | 60 | 140 |  |  |  | + | + | + | + |
|  |  | 80 | 176 |  |  |  |  | + |  |  |
|  |  | 100 | 212 |  |  |  |  | + |  |  |
|  |  | 120 | 248 |  |  |  |  | - |  |  |
| Sodium cyanide NaCN |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | + | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ | + | + |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Sodium Dithionite Na2S2O4 | 10 | 20 | 68 | ++ |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 |  |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Sodium ferricyanide Na3[Fe(CN)6]H2O | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | + | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | + | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Sodium ferrocyanide Na4[Fe(NC)6]10H2O | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | + | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | + | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |

Chemical Resistance

Chemical Resistance

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Sodium fluoride NaF |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  | ++ | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  | ++ | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Sodium hydrogen carbonate Na2HCO3 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ | + | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Sodium hydrogen sulfate NaHSO4 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Sodium hydroxide NaOH | 5 | 20 | 68 | + | + |  |  |  |  |  |
|  |  | 40 | 104 | + | -- |  |  |  |  |  |
|  |  | 60 | 140 | + | -- |  |  |  |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Sodium hydroxide NaOH | 15 | 20 | 68 | ++ | + | ++ | ++ | ++ | ++ | - |
|  |  | 40 | 104 | ++ | - | ++ | ++ | ++ | ++ | - |
|  |  | 60 | 140 | ++ | - | ++ | + | ++ | ++ | -- |
|  |  | 80 | 176 |  | -- | + | - | ++ | + |  |
|  |  | 100 | 212 |  |  |  | -- | ++ | + |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Sodium hydroxide NaOH | 30 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | - |
|  |  | 40 | 104 | ++ | ++ | ++ | + | ++ | ++ | -- |
|  |  | 60 | 140 | ++ | ++ | ++ | - | ++ | ++ |  |
|  |  | 80 | 176 |  | + | + | -- | ++ | ++ |  |
|  |  | 100 | 212 |  |  |  |  | ++ | + |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Sodium hydroxide NaOH | 50 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | -- |
|  |  | 40 | 104 | ++ | ++ | ++ | + | ++ | ++ |  |
|  |  | 60 | 140 | ++ | + | ++ | - | ++ | ++ |  |
|  |  | 80 | 176 |  | - | + | -- | ++ | ++ |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Sodium hypochlorite NaClO | 3 | 20 | 68 | ++ | ++ | + | ++ | ++ | + | ++ |
|  |  | 40 | 104 | ++ | ++ | + | ++ | ++ | + | + |
|  |  | 60 | 140 | - | - | + | ++ | ++ | - | + |
|  |  | 80 | 176 |  |  |  | ++ |  |  |  |
|  |  | 100 | 212 |  |  |  | ++ |  |  |  |
|  |  | 120 | 248 |  |  |  | ++ |  |  |  |
| Sodium hypochlorite NaClO | 5 | 20 | 68 | ++ | ++ | + | ++ | ++ | + | ++ |
|  |  | 40 | 104 | ++ | ++ | + | ++ | ++ | + | + |
|  |  | 60 | 140 | - | - | - | ++ | ++ | - | - |
|  |  | 80 | 176 |  |  |  | ++ |  |  |  |
|  |  | 100 | 212 |  |  |  | ++ |  |  |  |
|  |  | 120 | 248 |  |  |  | ++ |  |  |  |
| Sodium hypochlorite NaClO | 7 | 20 | 68 | ++ | ++ | + | ++ | ++ | + | ++ |
|  |  | 40 | 104 | ++ | ++ | - | ++ | ++ | - | + |
|  |  | 60 | 140 | - | - | - | ++ | ++ | - | - |
|  |  | 80 | 176 |  |  |  | ++ |  |  |  |
|  |  | 100 | 212 |  |  |  | ++ |  |  |  |
|  |  | 120 | 248 |  |  |  | ++ |  |  |  |
| Sodium hypochlorite NaClO | 10 | 20 | 68 | ++ | ++ | + | ++ | ++ | -- | ++ |
|  |  | 40 | 104 | ++ | ++ | - | ++ | ++ |  |  |
|  |  | 60 | 140 | - | - | - | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ |  |  |  |
|  |  | 100 | 212 |  |  |  | ++ |  |  |  |
|  |  | 120 | 248 |  |  |  | ++ |  |  |  |
| Sodium hypochlorite NaClO | 13 | 20 | 68 | ++ | ++ | + | ++ | ++ | -- | ++ |
|  |  | 40 | 104 | ++ | ++ | - | ++ | ++ |  |  |
|  |  | 60 | 140 | - | - |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ |  |  |  |
|  |  | 100 | 212 |  |  |  | ++ |  |  |  |
|  |  | 120 | 248 |  |  |  | ++ |  |  |  |

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Sodium iodide NaI |  | 20 | 68 | ++ |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 |  |  |  | + | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Sodium metasilicate Na2SiO3 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ | + | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Sodium nitrate NaNO3 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | + |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Sodium nitrite NaNO2 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | + | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Sodium palmitate C15H31COONa | 5 | 20 | 68 |  |  |  | ++ | ++ |  |  |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Sodium perborate NaBO3 · 4H2O |  | 20 | 68 |  |  |  | ++ | ++ | ++ |  |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Sodium perchlorate NaClO4 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ |  |  |
|  |  | 60 | 140 | + | ++ | ++ | ++ | ++ |  |  |
|  |  | 80 | 176 |  | + | + | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Sodium peroxide Na2O2 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ |  |  |
|  |  | 60 | 140 | + | ++ | ++ | ++ | ++ |  |  |
|  |  | 80 | 176 |  | + | + | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Sodium persulfate Na2S2O8 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | + |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  |  | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Sodium phosphate NaH2PO4 · 2H2O |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + |  | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | + |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Sodium phosphate Na2HPO4 · 12H2O |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | + |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Sodium phosphate Na3PO4 · 12H2O |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Sodium silicofluoride Na2SiF6 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | + | ++ |  |  |
| Sodium sulfate Na2SO4 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Sodium sulfide Na2S |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Sodium sulfite Na2SO3 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | + | + |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Sodium thiocyanate NaSCN |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | + | ++ |  |  |
| Sodium thiosulfate Na2S2O3 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ | + | ++ |
|  |  | 120 | 248 |  |  |  | + | ++ |  |  |
| Soybean oil |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | + | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | + | ++ | ++ | - | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ | -- | - |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  | -- |
| Stannic chloride (Tin( Ⅳ ) chloride) SnCl4 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | + | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Stannous chloride (Tin( Ⅱ ) chloride) SnCl2 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | + | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Stearic acid CH3(CH2)16COOH |  | 20 | 68 | ++ | ++ | + | ++ | ++ | - | ++ |
|  |  | 40 | 104 | ++ | ++ | + | ++ | ++ |  | ++ |
|  |  | 60 | 140 | ++ | ++ | + | ++ | ++ |  | - |
|  |  | 80 | 176 |  | + | + | ++ | ++ |  | - |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Styrene monomer C6H5CH=CH2 |  | 20 | 68 |  |  |  | ++ | ++ | -- | + |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Sulfomic acid HSO2NH2 | 20 | 20 | 68 | -- | -- | -- | -- |  |  |  |
|  |  | 40 | 104 |  |  |  |  |  |  |  |
|  |  | 60 | 140 |  |  |  |  |  |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Sulfonated caster oil |  | 20 | 68 | ++ |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 |  |  |  |  |  |  |  |
|  |  | 60 | 140 |  |  |  |  |  |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Sulfur S |  | 20 | 68 | ++ | ++ |  | ++ | ++ | - | ++ |
|  |  | 40 | 104 | ++ | ++ |  | ++ | ++ |  |  |
|  |  | 60 | 140 | + | ++ |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  | + |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Sulfur chloride S2Cl2 |  | 20 | 68 |  |  | - | ++ | ++ | -- | ++ |
|  |  | 40 | 104 |  |  | -- | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Sulfur dichloride SCl2 |  | 20 | 68 |  |  | - | ++ | ++ | -- | ++ |
|  |  | 40 | 104 |  |  | -- | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Sulfur dioxide SO2 | Dry | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | + | ++ | ++ | ++ | ++ | ++ |  |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | + |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ | + |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Sulfur dioxide SO2 | Wet | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | + | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | + | ++ | ++ | ++ |  |
|  |  | 100 | 212 |  | -- | + | ++ | ++ | + |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Sulfuric acid H2SO4 | 10 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Sulfuric acid H2SO4 | 30 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | + | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ | -- | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Sulfuric acid H2SO4 | 50 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | + | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ | -- | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Sulfuric acid H2SO4 | 60 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | + | ++ | ++ | - | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ | -- | + |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Sulfuric acid H2SO4 | 70 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | + | ++ |
|  |  | 80 | 176 |  | ++ | + | + | ++ | -- | ++ |
|  |  | 100 | 212 |  |  |  | + | ++ |  | + |
|  |  | 120 | 248 |  |  |  | - | + |  |  |
| Sulfuric acid H2SO4 | 80 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | + | + | + | ++ | ++ | + | ++ |
|  |  | 80 | 176 |  | - | + | + | ++ | - | + |
|  |  | 100 | 212 |  |  |  | + | ++ |  | - |
|  |  | 120 | 248 |  |  |  | - | + |  |  |

Chemical Resistance

Chemical Resistance

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Sulfuric acid H2SO4 | 90 | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | + | ++ | ++ | ++ | ++ | + | ++ |
|  |  | 60 | 140 | + | + | + | ++ | ++ | - | ++ |
|  |  | 80 | 176 |  | - | + | ++ | ++ | -- | + |
|  |  | 100 | 212 |  |  |  | + | + |  | -- |
|  |  | 120 | 248 |  |  |  | + | + |  |  |
| Sulfuric acid H2SO4 | 98 | 20 | 68 | + | + | -- | -- | ++ | -- | - |
|  |  | 40 | 104 | - | - |  |  | ++ |  |  |
|  |  | 60 | 140 | -- | -- |  |  | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | + |  |  |
|  |  | 120 | 248 |  |  |  |  | + |  |  |
| Sulfuric anhydride SO3 |  | 20 | 68 | -- | -- | -- | -- | + | -- | -- |
|  |  | 40 | 104 |  |  |  |  |  |  |  |
|  |  | 60 | 140 |  |  |  |  |  |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Sulfurous acid H2SO3 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | + | ++ |
|  |  | 80 | 176 |  | + | ++ | ++ | ++ | - | + |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | - |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Sulfuryl chloride SO2Cl2 | Pure | 20 | 68 | -- | -- |  | + | ++ | -- | ++ |
|  |  | 40 | 104 |  |  |  | - | ++ |  |  |
|  |  | 60 | 140 |  |  |  |  | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Sumition® (Insecticide) |  | 20 | 68 | -- | -- | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 |  |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 |  |  | + | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | + | ++ |  |  |
|  |  | 120 | 248 |  |  |  | + | ++ |  |  |
| Tall oil |  | 20 | 68 | ++ | ++ |  | ++ | ++ | -- | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Tannic acid C76H52O46 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | + | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ |  |  |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  | ++ | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Tar | Satu | 20 | 68 | -- | -- | + | ++ | ++ | -- | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Tartaric acid (Dioxysuccinic acid) CH(OH)COOH CH(OH)COOH |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | + | + | + | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | - | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  | -- | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Tertiary butyl alcohol (CH3)3COH |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | + | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Tetra chloroethylene Cl2C=CCl2 | Pure | 20 | 68 | -- | -- | + | ++ | ++ | -- | ++ |
|  |  | 40 | 104 |  |  | - | ++ | ++ |  | ++ |
|  |  | 60 | 140 |  |  | -- | ++ | ++ |  | -- |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Tetrachloroethane Cl2CHCHCl2 | pure | 20 | 68 | -- | -- | + | ++ | ++ | -- | + |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Tetraethyl lead Pb(C2H5)4 | Pure | 20 | 68 | ++ |  | ++ | ++ | ++ | -- | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Tetrahydrofuran C4H8O | Pure | 20 | 68 | -- | -- | + | - | ++ | -- | -- |
|  |  | 40 | 104 |  |  | - | -- | ++ |  |  |
|  |  | 60 | 140 |  |  | -- |  | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | + |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Tetraline(Tetrahydro naphthalene) C10H12 | Pure | 20 | 68 | -- | -- | -- | ++ | ++ | -- | ++ |
|  |  | 40 | 104 |  |  |  |  |  |  |  |
|  |  | 60 | 140 |  |  |  |  |  |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Titanic sulfate Ti(SO4)2 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ |  |  |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Titanium tetrachloride TiCl4 |  | 20 | 68 | + | + | + | ++ | ++ | -- | ++ |
|  |  | 40 | 104 |  |  |  |  |  |  | ++ |
|  |  | 60 | 140 |  |  |  |  |  |  | ++ |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Titanous sulfate Ti2(SO4)3 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ |  |  |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Toluene(Toluol) C6H5CH3 |  | 20 | 68 | -- | -- | ++ | ++ | ++ | -- | - |
|  |  | 40 | 104 |  |  | - | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  | -- | + | ++ |  |  |
|  |  | 80 | 176 |  |  |  | + | ++ |  |  |
|  |  | 100 | 212 |  |  |  | - | + |  |  |
|  |  | 120 | 248 |  |  |  |  | - |  |  |
| Triacetin C3H5(OCOCH3)3 | Pure | 20 | 68 |  |  |  |  | ++ | ++ | + |
|  |  | 40 | 104 |  |  |  |  | ++ |  |  |
|  |  | 60 | 140 |  |  |  |  | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Tributyl phosphate (C4H9O)3PO |  | 20 | 68 | -- |  | + | ++ | ++ | + | -- |
|  |  | 40 | 104 |  |  | + | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  | - | - | ++ |  |  |
|  |  | 80 | 176 |  |  |  | -- |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Trichloroacetic acid Cl3CCOOH |  | 20 | 68 |  |  | ++ | ++ | ++ | - | - |
|  |  | 40 | 104 |  |  | ++ | + | ++ |  |  |
|  |  | 60 | 140 |  |  | + | - | ++ |  |  |
|  |  | 80 | 176 |  |  |  | -- |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Trichloroethylene ClHC=CCl2 |  | 20 | 68 | -- | -- | + | ++ | ++ | -- | - |
|  |  | 40 | 104 |  |  | - | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  | -- | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Xylene C6H4(CH3)2 |  | 20 | 68 | -- | -- | -- | ++ | ++ | -- | + |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Yellow Phosphorus P4 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ |  |  |
|  |  | 40 | 104 |  |  |  |  |  |  |  |
|  |  | 60 | 140 |  |  |  |  |  |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Zinc acetate (CH3COO)2Zn |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Zinc bromide ZnBr2 | Satu | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Zinc chloride ZnCl2 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Zinc cyanide Zn(CN)2 |  | 20 | 68 | ++ |  | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Zinc nitrate Zn(NO3)2 · 6H2O |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Zinc sulfate ZnSO4 |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  | ++ |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |

| Chemicals | Concentration | Temp.(˚C) | Temp.(˚F) | PVC | CPVC | PP | PVDF | PTFE | EPDM | FKM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Tricresyl phosphate (CH3C6H4O)3PO | Pure | 20 | 68 | -- | -- | - | ++ | ++ | - | + |
|  |  | 40 | 104 |  |  |  |  | ++ |  |  |
|  |  | 60 | 140 |  |  |  |  | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Triethanolamine N(CH2CH2OH)3 |  | 20 | 68 | -- | -- | -- | -- | ++ | ++ | -- |
|  |  | 40 | 104 |  |  |  |  |  |  |  |
|  |  | 60 | 140 |  |  |  |  |  |  |  |
|  |  | 80 | 176 |  |  |  |  |  |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Triethylamine (C2H5)3N |  | 20 | 68 | + | -- | - | + | ++ | -- | - |
|  |  | 40 | 104 |  |  |  | - | ++ |  |  |
|  |  | 60 | 140 |  |  |  | -- | ++ |  |  |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |
| Turbine oil(#140) |  | 20 | 68 | ++ | ++ | + | ++ | ++ | -- | ++ |
|  |  | 40 | 104 |  |  |  |  | ++ |  | ++ |
|  |  | 60 | 140 |  |  |  |  | ++ |  | ++ |
|  |  | 80 | 176 |  |  |  |  | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Turpentine oil |  | 20 | 68 | ++ | ++ | + | ++ | ++ | + | + |
|  |  | 40 | 104 |  |  | - | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  | -- | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Urea CO(NH2)2 | Pure | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Urine |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Vaseline(Petrolatum) |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | -- | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ |  |  |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ |  |  |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| Vineger |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | + | ++ | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | + | ++ |  |  |
|  |  | 120 | 248 |  |  |  | + | ++ |  |  |
| Vinyl acetate CH3COOCH=CH2 |  | 20 | 68 | -- | -- | + | ++ | ++ | + | -- |
|  |  | 40 | 104 |  |  | + | ++ | ++ | -- |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  |  | ++ |  |  |
| Water (Potable water) |  | 20 | 68 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 40 | 104 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 60 | 140 | ++ | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 80 | 176 |  | ++ | ++ | ++ | ++ | ++ | ++ |
|  |  | 100 | 212 |  |  |  | ++ | ++ |  |  |
|  |  | 120 | 248 |  |  |  | ++ | ++ |  |  |
| White acid | Pure | 20 | 68 |  |  |  | ++ | ++ |  |  |
|  |  | 40 | 104 |  |  |  | ++ | ++ |  |  |
|  |  | 60 | 140 |  |  |  | ++ | ++ |  |  |
|  |  | 80 | 176 |  |  |  | ++ | ++ |  |  |
|  |  | 100 | 212 |  |  |  |  |  |  |  |
|  |  | 120 | 248 |  |  |  |  |  |  |  |

Chemical Resistance

6

Safety Precautions

Failure to follow the safety precautions below may result in misapplication or improper installation and testing which can cause severe personal injury and/

or property damage.

! WARNING

Safety Precautions