## Bkgrnd.
State Point Analysis
Spreadsheet developed by Eric J. Wahlberg, Ph.D., Brown and Caldwell
A state point analysis is a powerful activated sludge design, operations, and
troubleshooting tool. The traditional approach to a state point analysis is to
develop the requiste settling flux curve using the settling parameters Vo and K
(worksheet VoK). Alternatively, the requiste settling flux curve can be developed
using correlations between these settling parameters and SVI. The SVI is
performed a number of different ways: (1) in a 1 L graduated cylinder with
stirring (SVIGS), (2) in a 1 L graduated cylinder without stirring (SVIGN), (3) in a 2 L
settlometer with stirring (SVISS), and (4) in a 2 L settlometer without stirring
(SVISN). The appropriate correlations are used to generate the flux curves on the
following worksheets (labeled SVIGS, SVIGN, SVISS, and SVISN, respectively).
When you start this template, first choose the worksheet corresponding to the
settling data you have. For example, if you have settling velocity:solids concentration
(i.e., Vs:X) data from which you can estimate Vo and k in the equation,
Vs = Vo e-KX ,
you would use the VoK worksheet, or if you had SVI data that was generated using an
unstirred 2-L settlometer, you would use the SVISN worksheet.
Once in the desired worksheet, the first step to take is to choose the units you are
interested in. This is done by replacing the "0" with a "1" across from the desired
units. You then must fill in the following to generate a flux curve and a state point
analysis: the SVI, the number of secondary clarifiers, the area of each, the MLSS
concentration, the influent flow, and the RAS flow (remember to watch your units).
The curve and operating lines will appear on the plot.
If you would like to investigate other flow rates, enter them (one at a time) in the
alternate influent flow row. This will allow you to see the impact of different flows on the
system (e.g., ADWF versus PWWF). Similarly, you can see the impact of different
RAS flows by entering different RAS flows in the alternate RAS flow row. It's not a
good idea to investigate alternate influent flows and RAS flows at the same time
(which is to say that is not the way I have set it up).
To print the plot, double click on the plot before choosing "Print" in the File menu. If
you print the spreadsheet, the print area is set to include the plot (on a smaller scale
than if you print the plot by itself) and a table of summary information that you will
find useful, like surface overflow rates, solids loading rates, predicted RAS solids
concentrations, etc.
The correlations between the SVIs and the settling parameters, Vo and K, were
developed by the author while he was a graduate student at Clemson University,
Clemson, South Carolina. This work can be referenced in the following two
publications.
Wahlberg, E.J. and T.M. Keinath (1988). "Development of settling flux curves using
SVI." Journal Water Pollution Control Federation, 60, 2095.
Wahlberg, E.J. and T.M. Keinath (1995). "Development of settling flux curves using
SVI: An addendum." Water Environment Research, 67, 872.

## SVISN
This spreadsheet will generate a flux curve given the
following inputs (yellow cells, note units). | [7 empty] | 2 L Settlometer Without Stirring (SVISN) |  | (This is the sheet you are most likely to use.)
SVISN | 140 | mL/g
No. of clarifiers | 3 |  |  |  | alpha= | 0.261 | L/g
Area of each | 21382 | ft2 |  |  | beta= | 0.00166 | L/mL
MLSS | 4.3 | g/L |  |  | delta= | 0.0037 | g/mL
Influent flow | 36 | mgd |  |  | gamma= | 14.9 | m/h
RAS flow | 9 | mgd
Alternate influent flow | 0 | mgd
Alternate RAS flow | 0 | mgd
Choose desired flux units by
placing a "1" in place of
the "0" next to desired units:
kg/m2h | 0
kg/m2d | 0
lb/ft2d | 1
Influent | 3500 | gpm
Influent | 5.04 | mgd
RAS | 2261 | gpm
RAS | 3.2558 | mgd
Alternate influent | 3500 | gpm
Alternate influent | 5.04 | mgd
Alternate RAS flow | 1800 | gpm
Alternate RAS flow | 2.592 | mgd
X | G |  |  | Summary Information
Solids Concentration (g/L) | Solids Flux (lb/ft2d)
0 | 0 |  |  | SVISN |  |  | 140 | mL/g
0.1 | 4.1493 |  |  | Total Clarifier Surface Area |  |  | 64146 | ft2
0.2 | 7.8992 |  |  | MLSS Concentration |  |  | 4300 | mg/L
0.3 | 11.2783 |  |  | Influent Flow |  |  | 36 | mgd
0.4 | 14.3138 |  |  | Surface Overflow Rate |  |  | 561.2197 | gal/ft2d
0.5 | 17.0309 |  |  | RAS Flow |  |  | 9 | mgd
0.6 | 19.4531 |  |  | Applied Solids Loading* |  |  | 25.1517 | lb/ft2d
0.7 | 21.6027 |  |  | RAS SS Concentration* |  |  | 21500 | mg/L
0.8 | 23.5002 |  |  | Alternate Influent Flow |  |  | 0 | mgd
0.9 | 25.165 |  |  | Alt. Surface Overflow Rate |  |  | 0 | gal/ft2d
1 | 26.615 |  |  | Alt. Applied Solids Loading* |  |  | 0 | lb/ft2d
1.1 | 27.867 |  |  | Alt. RAS SS Concentration* |  |  | 0 | mg/L
1.2 | 28.9368 |  |  | Alternate RAS Flow |  |  | 0 | mgd
1.3 | 29.8391 |  |  | Alt. Applied Solids Loading* |  |  | 0 | lb/ft2d
1.4 | 30.5873 |  |  | Alt. RAS SS Concentration* |  |  | 0 | mg/L
1.5 | 31.1944
1.6 | 31.6722 |  |  | *Assumes underloaded conditions;check flux curve
1.7 | 32.0316
1.8 | 32.283
1.9 | 32.436
2 | 32.4994
2.1 | 32.4815
2.2 | 32.3901
2.3 | 32.2321
2.4 | 32.0143
2.5 | 31.7428
2.6 | 31.4232
2.7 | 31.0608
2.8 | 30.6605
2.9 | 30.2267
3 | 29.7636
3.1 | 29.2751
3.2 | 28.7646
3.3 | 28.2354
3.4 | 27.6905
3.5 | 27.1326
3.6 | 26.5643
3.7 | 25.9878
3.8 | 25.4052
3.9 | 24.8185
4 | 24.2294
4.1 | 23.6396
4.2 | 23.0503
4.3 | 22.463
4.4 | 21.8788
4.5 | 21.2988
4.6 | 20.724
4.7 | 20.1551
4.8 | 19.593
4.9 | 19.0382
5 | 18.4915
5.1 | 17.9533
5.2 | 17.4241
5.3 | 16.9042
5.4 | 16.394
5.5 | 15.8937
5.6 | 15.4036
5.7 | 14.9238
5.8 | 14.4546
5.9 | 13.9959
6 | 13.5479
6.1 | 13.1106
6.2 | 12.684
6.3 | 12.2681
6.4 | 11.8629
6.5 | 11.4682
6.6 | 11.084
6.7 | 10.7103
6.8 | 10.3468
6.9 | 9.9935
7 | 9.6503
7.1 | 9.3169
7.2 | 8.9933
7.3 | 8.6792
7.4 | 8.3745
7.5 | 8.0791
7.6 | 7.7927
7.7 | 7.5151
7.8 | 7.2462
7.9 | 6.9858
8 | 6.7336
8.1 | 6.4896
8.2 | 6.2534
8.3 | 6.025
8.4 | 5.804
8.5 | 5.5903
8.6 | 5.3838
8.7 | 5.1842
8.8 | 4.9913
8.9 | 4.805
9 | 4.6251
9.1 | 4.4514
9.2 | 4.2836
9.3 | 4.1217
9.4 | 3.9655
9.5 | 3.8147
9.6 | 3.6693
9.7 | 3.529
9.8 | 3.3938
9.9 | 3.2633
10 | 3.1376
10.1 | 3.0164
10.2 | 2.8996
10.3 | 2.7871
10.4 | 2.6787
10.5 | 2.5742
10.6 | 2.4736
10.7 | 2.3768
10.8 | 2.2835
10.9 | 2.1937
11 | 2.1072
11.1 | 2.024
11.2 | 1.9439
11.3 | 1.8669
11.4 | 1.7927
11.5 | 1.7214
11.6 | 1.6527
11.7 | 1.5867
11.8 | 1.5233
11.9 | 1.4622
12 | 1.4035
12.1 | 1.3471
12.2 | 1.2928
12.3 | 1.2407
12.4 | 1.1905
12.5 | 1.1424
12.6 | 1.0961
12.7 | 1.0516
12.8 | 1.0088
12.9 | 0.96777
13 | 0.92832
13.1 | 0.89043
13.2 | 0.85403
13.3 | 0.81907
13.4 | 0.7855
13.5 | 0.75327
13.6 | 0.72231
13.7 | 0.69259
13.8 | 0.66406
13.9 | 0.63667
14 | 0.61038
14.1 | 0.58515
14.2 | 0.56093
14.3 | 0.53768
14.4 | 0.51538
14.5 | 0.49397
14.6 | 0.47343
14.7 | 0.45373
14.8 | 0.43482
14.9 | 0.41669
15 | 0.39929
4.3 |  | 20.1214
0 |  |  | 0
8.6823 |  |  | 40.6278
0 |  |  |  | 25.1517
21.5 |  |  |  | 2.6633e-08
4.3 |  |  |  |  | 0
0 | [5 empty] | 0
0 | [5 empty] | 0
0 | [6 empty] | 0
0 | [6 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [8 empty] | 0
0 | [8 empty] | 0
I have used fxRender (www.codecogs.com/fxrender) to show how the solids flux is calculated.

## SVI & SA
SSV at 30 min | 400 | mL
MLSS | 2500 | mg/L
SVI | 160 | mL/g
Surface Area
Tank diameter | 165 | ft
Surface area | 21382.4469 | ft2

## SVIGN
This spreadsheet will generate a flux curve given the
following inputs (insert value in the appropriate cell
between thick lines -- mind your units): | [7 empty] | 1 L Graduated Cylinder Without Stirring (SVIGN) |  | In place of a tall, narrow graduated cylinder, use a 1 liter beaker.
SVIGN |  | 270 | mL/g
No. of clarifiers |  | 2 |  |  | alpha= | 0.351 | L/g
Area of each |  | 5672 | ft2 |  | beta= | 0.00058 | L/mL
MLSS |  | 2.89 | g/L |  | delta= | 0.00602 | g/mL
Inf. flow |  | 4.32 | mgd |  | gamma= | 18.2 | m/h
RAS flow |  | 1.872 | mgd
Alternate inf. flow |  | 0 | mgd
Alternate RAS flow |  | 0 | mgd
Choose desired flux units by |  | `
placing a "1" in place of
the "0" next to desired units:
kg/m2h | 0
kg/m2d | 0
lb/ft2d | 1
Influent flow | 3000 | gpm
| 4.32 | mgd
Combined RAS flow | 1300 | gpm
| 1.872 | mgd
X | G |  |  | Summary Information
Solids Concentration (g/L) | Solids Flux (lb/ft2d)
0 | 0 |  |  | SVIGN |  |  | 270 | mL/g
0.1 | 1.6723 |  |  | Total Clarifier Surface Area |  |  | 11344 | ft2
0.2 | 3.179 |  |  | MLSS Concentration |  |  | 2890 | mg/L
0.3 | 4.5325 |  |  | Influent Flow |  |  | 4.32 | mgd
0.4 | 5.7443 |  |  | Surface Overflow Rate |  |  | 380.8181 | gal/ft2d
0.5 | 6.825 |  |  | RAS Flow |  |  | 1.872 | mgd
0.6 | 7.7846 |  |  | Applied Solids Loading* |  |  | 13.1528 | lb/ft2d
0.7 | 8.6325 |  |  | RAS SS Concentration* |  |  | 9559.2308 | mg/L
0.8 | 9.3775 |  |  | Alternate Influent Flow |  |  | 0 | mgd
0.9 | 10.0275 |  |  | Alt. Surface Overflow Rate |  |  | 0 | gal/ft2d
1 | 10.5903 |  |  | Alt. Applied Solids Loading* |  |  | 0 | lb/ft2d
1.1 | 11.0727 |  |  | Alt. RAS SS Concentration* |  |  | 0 | mg/L
1.2 | 11.4815 |  |  | Alternate RAS Flow |  |  | 0 | mgd
1.3 | 11.8227 |  |  | Alt. Applied Solids Loading* |  |  | 0 | lb/ft2d
1.4 | 12.102 |  |  | Alt. RAS SS Concentration* |  |  | 0 | mg/L
1.5 | 12.3246
1.6 | 12.4956 |  |  | *Assumes underloaded conditions;check flux curve
1.7 | 12.6195
1.8 | 12.7005
1.9 | 12.7426
2 | 12.7494
2.1 | 12.7243
2.2 | 12.6704
2.3 | 12.5908
2.4 | 12.4879
2.5 | 12.3644
2.6 | 12.2226
2.7 | 12.0645
2.8 | 11.8921
2.9 | 11.7072
3 | 11.5115
3.1 | 11.3065
3.2 | 11.0936
3.3 | 10.874
3.4 | 10.649
3.5 | 10.4197
3.6 | 10.187
3.7 | 9.9517
3.8 | 9.7149
3.9 | 9.477
4 | 9.239
4.1 | 9.0012
4.2 | 8.7644
4.3 | 8.529
4.4 | 8.2954
4.5 | 8.064
4.6 | 7.8352
4.7 | 7.6093
4.8 | 7.3866
4.9 | 7.1673
5 | 6.9516
5.1 | 6.7397
5.2 | 6.5317
5.3 | 6.3279
5.4 | 6.1282
5.5 | 5.9327
5.6 | 5.7416
5.7 | 5.5549
5.8 | 5.3726
5.9 | 5.1947
6 | 5.0213
6.1 | 4.8524
6.2 | 4.6878
6.3 | 4.5277
6.4 | 4.3719
6.5 | 4.2204
6.6 | 4.0733
6.7 | 3.9303
6.8 | 3.7916
6.9 | 3.6569
7 | 3.5263
7.1 | 3.3996
7.2 | 3.2769
7.3 | 3.158
7.4 | 3.0428
7.5 | 2.9313
7.6 | 2.8233
7.7 | 2.7189
7.8 | 2.6179
7.9 | 2.5202
8 | 2.4258
8.1 | 2.3346
8.2 | 2.2464
8.3 | 2.1613
8.4 | 2.0791
8.5 | 1.9997
8.6 | 1.9231
8.7 | 1.8492
8.8 | 1.7779
8.9 | 1.7091
9 | 1.6427
9.1 | 1.5788
9.2 | 1.5171
9.3 | 1.4577
9.4 | 1.4005
9.5 | 1.3453
9.6 | 1.2922
9.7 | 1.241
9.8 | 1.1918
9.9 | 1.1443
10 | 1.0987
10.1 | 1.0548
10.2 | 1.0125
10.3 | 0.9718
10.4 | 0.93267
10.5 | 0.89504
10.6 | 0.85884
10.7 | 0.82404
10.8 | 0.79057
10.9 | 0.7584
11 | 0.72748
11.1 | 0.69776
11.2 | 0.6692
11.3 | 0.64176
11.4 | 0.61539
11.5 | 0.59007
11.6 | 0.56574
11.7 | 0.54238
11.8 | 0.51994
11.9 | 0.49839
12 | 0.47771
12.1 | 0.45785
12.2 | 0.43878
12.3 | 0.42049
12.4 | 0.40292
12.5 | 0.38607
12.6 | 0.3699
12.7 | 0.35438
12.8 | 0.33949
12.9 | 0.32521
13 | 0.31151
13.1 | 0.29837
13.2 | 0.28577
13.3 | 0.27368
13.4 | 0.26209
13.5 | 0.25098
13.6 | 0.24033
13.7 | 0.23011
13.8 | 0.22032
13.9 | 0.21093
14 | 0.20194
14.1 | 0.19331
14.2 | 0.18505
14.3 | 0.17713
14.4 | 0.16954
14.5 | 0.16227
14.6 | 0.1553
14.7 | 0.14862
14.8 | 0.14223
14.9 | 0.1361
15 | 0.13023
2.89 |  | 9.1764
0 |  |  | 0
5.0197 |  |  | 15.9385
0 |  |  |  | 13.1528
9.5592 |  |  |  | 1.3927e-08
2.89 |  |  |  |  | 0
0 | [5 empty] | 0
0 | [5 empty] | 0
0 | [6 empty] | 0
0 | [6 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [8 empty] | 0
0 | [8 empty] | 0

## SVIGS
This spreadsheet will generate a flux curve given the
following inputs (insert value in the appropriate cell |  |  |  |  | 1 L Graduated Cylinder With Stirring (SVIGS)
between thick lines -- mind your units):
SVIGS |  | 150 | mL/g
No. of clarifiers |  | 3 |  |  | alpha= | 0.245 | L/g
Area of each |  | 4776 | ft2 |  | beta= | 0.00296 | L/mL
MLSS |  | 3 | g/L |  | delta= | 0.01073 | g/mL
Inf. flow |  | 4.32 | mgd |  | gamma= | 24.3 | m/h
RAS flow |  | 2.16 | mgd
Alternate inf. flow |  | 0 | mgd
Alternate RAS flow |  | 0 | mgd
Choose desired flux units by
placing a "1" in place of
the "0" next to desired units:
kg/m2h | 0
kg/m2d | 0
lb/ft2d | 1
| Influent flow | 3000 | gpm
|  | 4.32 | mgd
| Combined RAS flow | 1500 | gpm
|  | 2.16 | mgd
X | G |  |  | Summary Information
Solids Concentration (g/L) | Solids Flux (lb/ft2d)
0 | 0 |  |  | SVIGS |  |  | 150 | mL/g
0.1 | 2.2278 |  |  | Total Clarifier Surface Area |  |  | 14328 | ft2
0.2 | 4.1589 |  |  | MLSS Concentration |  |  | 3000 | mg/L
0.3 | 5.823 |  |  | Influent Flow |  |  | 4.32 | mgd
0.4 | 7.2471 |  |  | Surface Overflow Rate |  |  | 301.5075 | gal/ft2d
0.5 | 8.4557 |  |  | RAS Flow |  |  | 2.16 | mgd
0.6 | 9.4713 |  |  | Applied Solids Loading* |  |  | 11.3127 | lb/ft2d
0.7 | 10.3141 |  |  | RAS SS Concentration* |  |  | 9000 | mg/L
0.8 | 11.0028 |  |  | Alternate Influent Flow |  |  | 0 | mgd
0.9 | 11.554 |  |  | Alt. Surface Overflow Rate |  |  | 0 | gal/ft2d
1 | 11.983 |  |  | Alt. Applied Solids Loading* |  |  | 0 | lb/ft2d
1.1 | 12.3037 |  |  | Alt. RAS SS Concentration* |  |  | 0 | mg/L
1.2 | 12.5286 |  |  | Alternate RAS Flow |  |  | 0 | mgd
1.3 | 12.6689 |  |  | Alt. Applied Solids Loading* |  |  | 0 | lb/ft2d
1.4 | 12.7351 |  |  | Alt. RAS SS Concentration* |  |  | 0 | mg/L
1.5 | 12.7363
1.6 | 12.6808 |  |  | *Assumes underloaded conditions;check flux curve
1.7 | 12.5763
1.8 | 12.4295
1.9 | 12.2465
2 | 12.0328
2.1 | 11.7932
2.2 | 11.5322
2.3 | 11.2537
2.4 | 10.9612
2.5 | 10.6577
2.6 | 10.346
2.7 | 10.0286
2.8 | 9.7076
2.9 | 9.3849
3 | 9.0621
3.1 | 8.7407
3.2 | 8.4219
3.3 | 8.1069
3.4 | 7.7964
3.5 | 7.4914
3.6 | 7.1924
3.7 | 6.9
3.8 | 6.6147
3.9 | 6.3367
4 | 6.0665
4.1 | 5.8042
4.2 | 5.5499
4.3 | 5.3037
4.4 | 5.0657
4.5 | 4.8359
4.6 | 4.6142
4.7 | 4.4006
4.8 | 4.1951
4.9 | 3.9973
5 | 3.8073
5.1 | 3.6249
5.2 | 3.4499
5.3 | 3.2821
5.4 | 3.1214
5.5 | 2.9676
5.6 | 2.8203
5.7 | 2.6796
5.8 | 2.545
5.9 | 2.4166
6 | 2.2939
6.1 | 2.1768
6.2 | 2.0652
6.3 | 1.9588
6.4 | 1.8574
6.5 | 1.7608
6.6 | 1.6689
6.7 | 1.5814
6.8 | 1.4981
6.9 | 1.4189
7 | 1.3437
7.1 | 1.2721
7.2 | 1.2041
7.3 | 1.1396
7.4 | 1.0783
7.5 | 1.0201
7.6 | 0.96487
7.7 | 0.91248
7.8 | 0.86279
7.9 | 0.81567
8 | 0.771
8.1 | 0.72866
8.2 | 0.68854
8.3 | 0.65054
8.4 | 0.61454
8.5 | 0.58045
8.6 | 0.54818
8.7 | 0.51763
8.8 | 0.48872
8.9 | 0.46137
9 | 0.43549
9.1 | 0.41101
9.2 | 0.38786
9.3 | 0.36597
9.4 | 0.34528
9.5 | 0.32572
9.6 | 0.30723
9.7 | 0.28977
9.8 | 0.27326
9.9 | 0.25767
10 | 0.24294
10.1 | 0.22904
10.2 | 0.2159
10.3 | 0.2035
10.4 | 0.1918
10.5 | 0.18075
10.6 | 0.17032
10.7 | 0.16048
10.8 | 0.1512
10.9 | 0.14244
11 | 0.13417
11.1 | 0.12638
11.2 | 0.11903
11.3 | 0.1121
11.4 | 0.10556
11.5 | 0.099394
11.6 | 0.093583
11.7 | 0.088105
11.8 | 0.082942
11.9 | 0.078076
12 | 0.07349
12.1 | 0.069169
12.2 | 0.065097
12.3 | 0.061261
12.4 | 0.057647
12.5 | 0.054243
12.6 | 0.051037
12.7 | 0.048017
12.8 | 0.045173
12.9 | 0.042494
13 | 0.039973
13.1 | 0.037598
13.2 | 0.035363
13.3 | 0.033258
13.4 | 0.031278
13.5 | 0.029413
13.6 | 0.027658
13.7 | 0.026006
13.8 | 0.024452
13.9 | 0.022989
14 | 0.021613
14.1 | 0.020318
14.2 | 0.0191
14.3 | 0.017954
14.4 | 0.016876
14.5 | 0.015861
14.6 | 0.014908
14.7 | 0.01401
14.8 | 0.013166
14.9 | 0.012373
15 | 0.011627
3 |  | 7.5418
0 |  |  | 0
6.3363 |  |  | 15.9291
0 |  |  |  | 11.3127
9 |  |  |  | 1.1979e-08
3 |  |  |  |  | 0
0 | [5 empty] | 0
0 | [5 empty] | 0
0 | [6 empty] | 0
0 | [6 empty] | 0
0 | [8 empty] | 0
0 | [8 empty] | 0

## SVISS
This spreadsheet will generate a flux curve given the
following inputs (insert value in the appropriate cell | [7 empty] | 2 L Settleometer With Stirring (SVISS)
between thick lines -- mind your units):
SVISS |  | 173 | mL/g
No. of clarifiers |  | 2 |  |  | alpha= | 0.211 | L/g
Area of each |  | 5776 | ft2 |  | beta= | 0.00236 | L/mL
MLSS |  | 3 | g/L |  | delta= | 0.00593 | g/mL
Inf. flow |  | 4.3 | mgd |  | gamma= | 14.6 | m/h
RAS flow |  | 1.8 | mgd
Alternate inf. flow |  | 0 | mgd
Alternate RAS flow |  | 0 | mgd
Choose desired flux units by
placing a "1" in place of
the "0" next to desired units:
kg/m2h | 0
kg/m2d | 0
lb/ft2d | 1
X | G |  |  | Summary Information
Solids Concentration (g/L) | Solids Flux (lb/ft2d)
0 | 0 |  |  | SVISS |  |  | 173 | mL/g
0.1 | 2.416 |  |  | Total Clarifier Surface Area |  |  | 11552 | ft2
0.2 | 4.5419 |  |  | MLSS Concentration |  |  | 3000 | mg/L
0.3 | 6.4038 |  |  | Influent Flow |  |  | 4.3 | mgd
0.4 | 8.0256 |  |  | Surface Overflow Rate |  |  | 372.2299 | gal/ft2d
0.5 | 9.4296 |  |  | RAS Flow |  |  | 1.8 | mgd
0.6 | 10.6361 |  |  | Applied Solids Loading* |  |  | 13.2084 | lb/ft2d
0.7 | 11.6636 |  |  | RAS SS Concentration* |  |  | 10166.6667 | mg/L
0.8 | 12.5294 |  |  | Alternate Influent Flow |  |  | 0 | mgd
0.9 | 13.2491 |  |  | Alt. Surface Overflow Rate |  |  | 0 | gal/ft2d
1 | 13.8373 |  |  | Alt. Applied Solids Loading* |  |  | 0 | lb/ft2d
1.1 | 14.307 |  |  | Alt. RAS SS Concentration* |  |  | 0 | mg/L
1.2 | 14.6704 |  |  | Alternate RAS Flow |  |  | 0 | mgd
1.3 | 14.9385 |  |  | Alt. Applied Solids Loading* |  |  | 0 | lb/ft2d
1.4 | 15.1216 |  |  | Alt. RAS SS Concentration* |  |  | 0 | mg/L
1.5 | 15.2288
1.6 | 15.2686 |  |  | *Assumes underloaded conditions;check flux curve
1.7 | 15.2487
1.8 | 15.1762
1.9 | 15.0574
2 | 14.8981
2.1 | 14.7036
2.2 | 14.4788
2.3 | 14.228
2.4 | 13.955
2.5 | 13.6636
2.6 | 13.3568
2.7 | 13.0376
2.8 | 12.7086
2.9 | 12.3721
3 | 12.0302
3.1 | 11.6847
3.2 | 11.3373
3.3 | 10.9895
3.4 | 10.6426
3.5 | 10.2978
3.6 | 9.956
3.7 | 9.618
3.8 | 9.2848
3.9 | 8.9569
4 | 8.635
4.1 | 8.3193
4.2 | 8.0105
4.3 | 7.7087
4.4 | 7.4143
4.5 | 7.1275
4.6 | 6.8484
4.7 | 6.5771
4.8 | 6.3137
4.9 | 6.0582
5 | 5.8106
5.1 | 5.5709
5.2 | 5.339
5.3 | 5.1149
5.4 | 4.8985
5.5 | 4.6896
5.6 | 4.4882
5.7 | 4.294
5.8 | 4.1069
5.9 | 3.9269
6 | 3.7536
6.1 | 3.587
6.2 | 3.4269
6.3 | 3.2731
6.4 | 3.1254
6.5 | 2.9836
6.6 | 2.8476
6.7 | 2.7171
6.8 | 2.5921
6.9 | 2.4723
7 | 2.3575
7.1 | 2.2476
7.2 | 2.1424
7.3 | 2.0417
7.4 | 1.9454
7.5 | 1.8533
7.6 | 1.7652
7.7 | 1.681
7.8 | 1.6006
7.9 | 1.5238
8 | 1.4504
8.1 | 1.3804
8.2 | 1.3135
8.3 | 1.2497
8.4 | 1.1888
8.5 | 1.1307
8.6 | 1.0753
8.7 | 1.0225
8.8 | 0.97213
8.9 | 0.92414
9 | 0.8784
9.1 | 0.83483
9.2 | 0.79332
9.3 | 0.75379
9.4 | 0.71614
9.5 | 0.6803
9.6 | 0.64618
9.7 | 0.6137
9.8 | 0.5828
9.9 | 0.55339
10 | 0.52541
10.1 | 0.4988
10.2 | 0.47349
10.3 | 0.44942
10.4 | 0.42653
10.5 | 0.40478
10.6 | 0.38409
10.7 | 0.36443
10.8 | 0.34575
10.9 | 0.328
11 | 0.31113
11.1 | 0.29511
11.2 | 0.27988
11.3 | 0.26543
11.4 | 0.2517
11.5 | 0.23866
11.6 | 0.22628
11.7 | 0.21452
11.8 | 0.20336
11.9 | 0.19277
12 | 0.18272
12.1 | 0.17318
12.2 | 0.16412
12.3 | 0.15553
12.4 | 0.14738
12.5 | 0.13965
12.6 | 0.13231
12.7 | 0.12535
12.8 | 0.11875
12.9 | 0.1125
13 | 0.10656
13.1 | 0.10093
13.2 | 0.095595
13.3 | 0.090535
13.4 | 0.085739
13.5 | 0.081191
13.6 | 0.076881
13.7 | 0.072796
13.8 | 0.068924
13.9 | 0.065255
14 | 0.061777
14.1 | 0.058482
14.2 | 0.05536
14.3 | 0.052403
14.4 | 0.0496
14.5 | 0.046946
14.6 | 0.044431
14.7 | 0.042049
14.8 | 0.039793
14.9 | 0.037656
15 | 0.035632
3 |  | 9.3108
0 |  |  | 0
6.1498 |  |  | 19.0866
0 |  |  |  | 13.2084
10.1667 |  |  |  | 1.3986e-08
3 |  |  |  |  | 0
0 | [5 empty] | 0
0 | [5 empty] | 0
0 | [6 empty] | 0
0 | [6 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [8 empty] | 0
0 | [8 empty] | 0

## VoK
This spreadsheet will generate a flux curve given the
following inputs (insert value in the appropriate cell
between thick lines -- mind your units):
Vo |  | 225 | m/d |  | 1 | ft | = | 0.3048 | m
K |  | 0.66 | L/g |  | 738 | ft | = | 224.9424 | m
No. of clarifiers |  | 2 |  |  | 6.15 | in/m | = | 738 | ft/d
Area of each |  | 908 | ft2
MLSS |  | 2.5 | g/L
Inf. flow |  | 1 | mgd
RAS flow |  | 0.7 | mgd
Alternate inf. flow |  | 2.5 | mgd
Alternate RAS flow |  | 1.4 | mgd
Choose desired flux units by
placing a "1" in place of
the "0" next to desired units:
kg/m2h | 0
kg/m2d | 0
lb/ft2d | 1
X | G |  |  | Summary Information
Solids Concentration (g/l) | Solids Flux (lb/ft2d)
0 | 0 |  |  | Vo |  |  | 225 | m/d
0.1 | 4.3102 |  |  | K |  |  | 0.66 | L/g
0.2 | 8.0697 |  |  | Total Clarifier Surface Area |  |  | 1816 | ft2
0.3 | 11.3315 |  |  | MLSS Concentration |  |  | 2.5 | mg/L
0.4 | 14.1437 |  |  | Influent Flow |  |  | 1 | mgd
0.5 | 16.5504 |  |  | Surface Overflow Rate |  |  | 550.6608 | gal/ft2d
0.6 | 18.592 |  |  | RAS Flow |  |  | 0.7 | mgd
0.7 | 20.3053 |  |  | Applied Solids Loading* |  |  | 19.5132 | lb/ft2d
0.8 | 21.7239 |  |  | RAS SS Concentration* |  |  | 6071.4286 | mg/L
0.9 | 22.8785 |  |  | Alternate Influent Flow |  |  | 2.5 | mgd
1 | 23.797 |  |  | Alt. Surface Overflow Rate |  |  | 1376.652 | gal/ft2d
1.1 | 24.5048 |  |  | Alt. Applied Solids Loading* |  |  | 36.7308 | lb/ft2d
1.2 | 25.0251 |  |  | Alt. RAS SS Concentration* |  |  | 11428.5714 | mg/L
1.3 | 25.379 |  |  | Alternate RAS Flow |  |  | 2.5 | mgd
1.4 | 25.5856 |  |  | Alt. Applied Solids Loading* |  |  | 27.5481 | kg/m2d
1.5 | 25.6623 |  |  | Alt. RAS SS Concentration* |  |  | 4285.7143 | mg/L
1.6 | 25.6248
1.7 | 25.4875 |  |  | *Assumes underloaded conditions;check flux curve
1.8 | 25.2631
1.9 | 24.9634
2 | 24.599
2.1 | 24.1793
2.2 | 23.7128
2.3 | 23.2073
2.4 | 22.6697
2.5 | 22.106
2.6 | 21.5219
2.7 | 20.9222
2.8 | 20.3113
2.9 | 19.6931
3 | 19.071
3.1 | 18.4481
3.2 | 17.8269
3.3 | 17.2098
3.4 | 16.5989
3.5 | 15.9957
3.6 | 15.4019
3.7 | 14.8187
3.8 | 14.2472
3.9 | 13.6882
4 | 13.1425
4.1 | 12.6107
4.2 | 12.0932
4.3 | 11.5904
4.4 | 11.1024
4.5 | 10.6295
4.6 | 10.1718
4.7 | 9.7291
4.8 | 9.3015
4.9 | 8.8888
5 | 8.4909
5.1 | 8.1076
5.2 | 7.7386
5.3 | 7.3836
5.4 | 7.0425
5.5 | 6.7147
5.6 | 6.4002
5.7 | 6.0984
5.8 | 5.809
5.9 | 5.5318
6 | 5.2662
6.1 | 5.0121
6.2 | 4.7689
6.3 | 4.5363
6.4 | 4.314
6.5 | 4.1015
6.6 | 3.8986
6.7 | 3.7049
6.8 | 3.5201
6.9 | 3.3437
7 | 3.1755
7.1 | 3.0152
7.2 | 2.8623
7.3 | 2.7167
7.4 | 2.5781
7.5 | 2.446
7.6 | 2.3203
7.7 | 2.2007
7.8 | 2.0869
7.9 | 1.9787
8 | 1.8757
8.1 | 1.7779
8.2 | 1.6849
8.3 | 1.5965
8.4 | 1.5125
8.5 | 1.4328
8.6 | 1.3571
8.7 | 1.2852
8.8 | 1.2169
8.9 | 1.1521
9 | 1.0907
9.1 | 1.0323
9.2 | 0.97703
9.3 | 0.92457
9.4 | 0.87482
9.5 | 0.82766
9.6 | 0.78296
9.7 | 0.74058
9.8 | 0.70043
9.9 | 0.66239
10 | 0.62634
10.1 | 0.5922
10.2 | 0.55987
10.3 | 0.52925
10.4 | 0.50026
10.5 | 0.47281
10.6 | 0.44683
10.7 | 0.42223
10.8 | 0.39896
10.9 | 0.37694
11 | 0.3561
11.1 | 0.33639
11.2 | 0.31774
11.3 | 0.3001
11.4 | 0.28342
11.5 | 0.26764
11.6 | 0.25273
11.7 | 0.23863
11.8 | 0.2253
11.9 | 0.21269
12 | 0.20078
12.1 | 0.18952
12.2 | 0.17889
12.3 | 0.16883
12.4 | 0.15934
12.5 | 0.15036
12.6 | 0.14188
12.7 | 0.13388
12.8 | 0.12631
12.9 | 0.11917
13 | 0.11242
13.1 | 0.10605
13.2 | 0.10004
13.3 | 0.094356
13.4 | 0.088994
13.5 | 0.083932
13.6 | 0.079153
13.7 | 0.074642
13.8 | 0.070385
13.9 | 0.066367
14 | 0.062575
14.1 | 0.058997
14.2 | 0.055621
14.3 | 0.052435
14.4 | 0.049429
14.5 | 0.046594
14.6 | 0.043918
14.7 | 0.041395
14.8 | 0.039015
14.9 | 0.03677
15 | 0.034652
2.5 |  | 11.4784
0 |  |  | 0
6.9869 |  |  | 32.0795
0 |  |  |  | 19.5132
6.0714 |  |  |  | 2.0662e-08
2.5 |  |  |  |  | 28.6959
0 | [5 empty] | 0
2.7948 | [5 empty] | 32.0795
0 | [6 empty] | 36.7308
11.4286 | [6 empty] | 3.8893e-08 |  |  | 36.7308
0 | [7 empty] | 27.5481 |  | #REF!
4.2857 | [7 empty] | 2.917e-08